## Points List
| Workbench | Mosaic | Mosaic | Mosaic | Mosaic | Mosaic | Mosaic | Func Spec | Func Spec | Func Spec/Mosaic | Func Spec/Mosaic | Func Spec/Mosaic | Func Spec/Mosaic | Func Spec/RTU | Workbench | Workbench | Func Spec/Mosaic | Func Spec | Workbench/E-Config | Workbench | Workbench | E-Config | E-Config | E-Config | E-Config | E-Config | Mosaic | Mosaic
Index | Tag (Actual RTU) | Plant | Desig | Quantity | Proposed UUTS Point Name | State 0 | State 1 | Point Description | Type | Units | Digital Alarm/Event (Priority) | Digital Trending | Analog Trending | Analog Event (RTU) | Sample Rate (s) | Deviation | Parameter Trending | Point Purpose | DNP Address | Data Type | Direction (wrt RTU) | Dnp3Object | Class | Transmission | AnalogEventDeviationChange | AnalogEventDeviationType | Trend TimebaseSec | Trend TimebaseNanosec
1 | stn1pbGenOpt | Site | 1 | Generator_opt_installed | Site : 1 : Generator_opt_installed | No | Yes | Option A – ATS & Generator Fitted | Digital Status | [7 empty] | Y | Parameter Feedback | 10064 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
2 | stn1pbPmp3Opt | Site | 1 | Pump_3_opt_installed | Site : 1 : Pump_3_opt_installed | No | Yes | Option D1 – MPC Pump 3 Fitted | Digital Status | [7 empty] | Y | Parameter Feedback | 10340 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
3 | stn1pbPmp4Opt | Site | 1 | Pump_4_opt_installed | Site : 1 : Pump_4_opt_installed | No | Yes | Option D2 – MPC Pump 4 Fitted | Digital Status | [7 empty] | Y | Parameter Feedback | 10360 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
4 | stn1pbPmp5Opt | Site | 1 | Pump_5_opt_installed | Site : 1 : Pump_5_opt_installed | No | Yes | Option D3 – MPC Pump 5 Fitted | Digital Status | [7 empty] | Y | Parameter Feedback | 10380 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
4.1 | TBA | TBA | TBA | TBA | TBA | No | Yes | Option D4 – MPC Jockey Pump Fitted | Digital Status | [7 empty] | Y | Parameter Feedback | TBA | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
5 | stn1pbFlw1Opt | Site | 1 | Flow_meter_1_opt_installed | Site : 1 : Flow_meter_1_opt_installed | No | Yes | Option E1 – Discharge Flowmeter Fitted | Digital Status | [7 empty] | Y | Parameter Feedback | 10055 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
6 | stn1pbFlw2Opt | Site | 1 | Flow_meter_2_opt_installed | Site : 1 : Flow_meter_2_opt_installed | No | Yes | Option E2 – Bypass Flowmeter Fitted | Digital Status | [7 empty] | Y | Parameter Feedback | 10056 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
6.1 | TBA | TBA | TBA | TBA | TBA | No | Yes | Option E3 – Redundant Discharge Pressure Transmitter Fitted | Digital Status | [7 empty] | Y | Parameter Feedback | TBA | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
7 | stn1pbLFireOpt | Site | 1 | Local_fire_opt_installed | Site : 1 : Local_fire_opt_installed | No | Yes | Option I – Fire Mode Switch Fitted | Digital Status | [7 empty] | Y | Parameter Feedback | 10063 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
8 | stn1pbPit1Opt | Site | 1 | Pump_pit_level_probe_opt_installed | Site : 1 : Pump_pit_level_probe_opt_installed | No | Yes | Option L1 – Pump Box Pit Level Probe | Digital Status | [7 empty] | Y | Parameter Feedback | 10065 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
9 | stn1pbPit2Opt | Site | 1 | Flow_meter_1_pit_level_probe_opt_installed | Site : 1 : Flow_meter_1_pit_level_probe_opt_installed | No | Yes | Option L2 – Flow Meter 1 Pit Level Probe | Digital Status | [7 empty] | Y | Parameter Feedback | 10066 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
10 | stn1pbPit3Opt | Site | 1 | Flow_meter_2_pit_level_probe_opt_installed | Site : 1 : Flow_meter_2_pit_level_probe_opt_installed | No | Yes | Option L3 – Flow Meter 2 Pit Level Probe | Digital Status | [7 empty] | Y | Parameter Feedback | 10067 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
11 | stn1pbPreVesOpt | Site | 1 | Pressure_vessel_opt_installed | Site : 1 : Pressure_vessel_opt_installed | No | Yes | Option Q – Pressure Vessel | Digital Status | [7 empty] | Y | Parameter Feedback | 10062 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
12 | stn1pbPeerPreModeOpt | Water_pumping_station | 1 | Peer_pressure_opt_installed | Water_pumping_station : 1 : Peer_pressure_opt_installed | No | Yes | Option R1 - Peer Pressure Mode | Digital Status | [7 empty] | Y | Parameter Feedback | 10016 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
13 | stn1pbSchDelModeOpt | Water_pumping_station | 1 | Scheduled_delivery_opt_installed | Water_pumping_station : 1 : Scheduled_delivery_opt_installed | No | Yes | Option R2 - Scheduled Pressure Mode | Digital Status | [7 empty] | Y | Parameter Feedback | 10019 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
14 | stn1pbFlwModModeOpt | Water_pumping_station | 1 | Flow_modulation_opt_installed | Water_pumping_station : 1 : Flow_modulation_opt_installed | No | Yes | Option R3 – Flow Modulation Mode | Digital Status | [7 empty] | Y | Parameter Feedback | 10029 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
14.1 | TBA | TBA | TBA | TBA | TBA | No | Yes | Option U - Emergency Stop Fitted | Digital Status | [7 empty] | Y | Parameter Feedback | TBA | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
14.2 | TBA | TBA | TBA | TBA | TBA | No | Yes | Option V - Emergency Stop Safety Function Failure Monitoring | Digital Status | [7 empty] | Y | Parameter Feedback | TBA | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
15 | stn1prRemModeSelDef | Site | 1 | Remote_mode_select_default | Site : 1 : Remote_mode_select_default |  |  | Station Remote Control Mode Select Default | Analog Status | [7 empty] | Y | Parameter Feedback | 10042 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
16 | stn1dsLocalModeActive | Water_pumping_station | 1 | Local_mode | Water_pumping_station : 1 : Local_mode | Off | Active | Station Local Mode | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10049 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
17 | stn1dsLocalFireModeActive | Water_pumping_station | 1 | Local_fire_mode | Water_pumping_station : 1 : Local_fire_mode | Off | Active | Station Local Fire Mode | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10050 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
18 | stn1dsDelPreModeActive | Water_pumping_station | 1 | Delivery_pressure_mode | Water_pumping_station : 1 : Delivery_pressure_mode | Off | Active | Delivery Pressure Mode | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10014 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
19 | stn1dsPeerPreModeActive | Water_pumping_station | 1 | Peer_pressure_mode | Water_pumping_station : 1 : Peer_pressure_mode | Off | Active | Peer Pressure Mode | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10017 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
20 | stn1dsSchDelModeActive | Water_pumping_station | 1 | Scheduled_delivery_mode | Water_pumping_station : 1 : Scheduled_delivery_mode | Off | Active | Scheduled Delivery Pressure Mode | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10020 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
21 | stn1dsFlwModModeActive | Water_pumping_station | 1 | Flow_modulation_mode | Water_pumping_station : 1 : Flow_modulation_mode | Off | Active | Flow Modulation Mode | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10030 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
22 | stn1dsRemFireModeActive | Water_pumping_station | 1 | Remote_fire_mode | Water_pumping_station : 1 : Remote_fire_mode | Off | Active | Remote Fire Mode | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10047 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
23 | stn1dsRemManModeActive | Water_pumping_station | 1 | Remote_manual_mode | Water_pumping_station : 1 : Remote_manual_mode | Off | Active | Remote Manual Mode | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10048 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
24 | stn1dsFixSpdModeActive | Water_pumping_station | 1 | Fixed_speed_mode | Water_pumping_station : 1 : Fixed_speed_mode | Off | Active | Fixed Speed Mode | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10051 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
25 | stn1asCtrlModeAct | Water_pumping_station | 1 | Control_mode | Water_pumping_station : 1 : Control_mode |  |  | Actual Station Mode Status Integer | Analog Status |  | Event (States defined in SCADA) |  | Y | Y |  |  |  | Analog Status | 10040 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
26 | stn1acRemModeSel | Water_pumping_station | 1 | Remote_mode_select | Water_pumping_station : 1 : Remote_mode_select |  |  | Station Remote Control Mode Select | Analog Control |  | Event (States defined in SCADA) | [6 empty] | Setpoint | 10504 | DINT | VarInput | g30v2 16bit Analog In | Class 0 | Static | None | None
27 | stn1asRemModeSelFbk | Water_pumping_station | 1 | Remote_mode_select_Fbk | Water_pumping_station : 1 : Remote_mode_select_Fbk |  |  | Station Remote Control Mode Select Feedback | Analog Status |  | Event (States defined in SCADA) |  | Y | Y |  |  |  | Setpoint Feedback | 10041 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
28 | zne1prPreDef | Water_pumping_station | 1 | Discharge_pressure_default | Water_pumping_station : 1 : Discharge_pressure_default |  |  | Zone Default Discharge Pressure | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15006 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
29 | zne1prPreMin | Water_pumping_station | 1 | Discharge_pressure_min | Water_pumping_station : 1 : Discharge_pressure_min |  |  | Zone Minimum Discharge Pressure | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15004 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
30 | zne1prPreMax | Water_pumping_station | 1 | Discharge_pressure_max | Water_pumping_station : 1 : Discharge_pressure_max |  |  | Zone Maximum Discharge Pressure | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15003 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
31 | stn1acDelPreModeSP | Water_pumping_station | 1 | Delivery_pressure_setpoint | Water_pumping_station : 1 : Delivery_pressure_setpoint |  |  | Delivery Pressure Setpoint | Analog Control | mAHD | [7 empty] | Setpoint | 15505 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
32 | stn1asDelPreModeSPFbk | Water_pumping_station | 1 | Delivery_pressure_setpoint_Fbk | Water_pumping_station : 1 : Delivery_pressure_setpoint_Fbk |  |  | Delivery Pressure Setpoint Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15032 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
33 | stn1dsPeerModeCtrlFltAlm | Water_pumping_station | 1 | Peer_pressure_control_fault | Water_pumping_station : 1 : Peer_pressure_control_fault | Ok | Fault | Peer Pressure Control Fault Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10018 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
34 | stn1prPeerModePre2Dev | Water_pumping_station | 1 | Peer_mode_delivery_pressure_deviation | Water_pumping_station : 1 : Peer_mode_delivery_pressure_deviation |  |  | Peer Mode Discharge Pressure Deviation | Analog Status | m | [6 empty] | Y | Parameter Feedback | 15247 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
35 | stn1acPeerPreModeSP | Water_pumping_station | 1 | Peer_pressure_setpoint | Water_pumping_station : 1 : Peer_pressure_setpoint |  |  | Peer Pressure Setpoint | Analog Control | mAHD | [7 empty] | Setpoint | 15507 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
36 | stn1asPeerPreModeSPFbk | Water_pumping_station | 1 | Peer_pressure_setpoint_Fbk | Water_pumping_station : 1 : Peer_pressure_setpoint_Fbk |  |  | Peer Pressure Setpoint Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15037 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
37 | pre3prAlmRange | Pressure_gauge | 3 | Alarm_range | Pressure_gauge : 3 : Alarm_range |  |  | Peer Pressure Alarm Range | Analog Status | m | [6 empty] | Y | Parameter Feedback | 15067 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
38
39 | stn1asPeerPreSysLoss | Water_pumping_station | 1 | Peer_mode_system_loss | Water_pumping_station : 1 : Peer_mode_system_loss |  |  | Peer Mode System Loss | Analog Status | m |  |  | Y | Y | 60 | 1 |  | Calculation | 15043 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
40 | stn1asPeerPreModeRPS2 | Water_pumping_station | 1 | Peer_mode_required_pressure_setpoint | Water_pumping_station : 1 : Peer_mode_required_pressure_setpoint |  |  | Peer Mode Required Pressure Setpoint (RPS2) | Analog Status | mAHD |  |  | Y | Y | 60 | 1 |  | Calculation | 15038 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
41 | stn1prPeerPreModeSPDef | Water_pumping_station | 1 | Peer_pressure_setpoint_default | Water_pumping_station : 1 : Peer_pressure_setpoint_default |  |  | Peer Pressure Setpoint Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15039 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
42 | stn1prPeerPreModeSPMax | Water_pumping_station | 1 | Peer_pressure_setpoint_max | Water_pumping_station : 1 : Peer_pressure_setpoint_max |  |  | Peer Pressure Setpoint Max | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15040 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
43 | stn1prPeerPreModeSPMin | Water_pumping_station | 1 | Peer_pressure_setpoint_min | Water_pumping_station : 1 : Peer_pressure_setpoint_min |  |  | Peer Pressure Setpoint Min | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15041 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
44 | stn1dsSchDelTabInv | Water_pumping_station | 1 | Scheduled_delivery_table_invalid | Water_pumping_station : 1 : Scheduled_delivery_table_invalid | Ok | Fault | Scheduled Delivery Mode Lookup Table Invalid | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10021 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
45 | stn1acSchDelR0Pre | Water_pumping_station | 1 | Scheduled_delivery_R0_pressure | Water_pumping_station : 1 : Scheduled_delivery_R0_pressure |  |  | Scheduled Delivery Window 0 Pressure Setpoint | Analog Control | mAHD | [7 empty] | Setpoint | 15509 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
46 | stn1acSchDelR1St | Water_pumping_station | 1 | Scheduled_delivery_R1_start_time | Water_pumping_station : 1 : Scheduled_delivery_R1_start_time |  |  | Scheduled Delivery Window 1 Start Time | Analog Control | Time | [7 empty] | Setpoint | 10506 | DINT | VarInput | g30v2 16bit Analog In | Class 0 | Static | None | None
47 | stn1acSchDelR1Pre | Water_pumping_station | 1 | Scheduled_delivery_R1_pressure | Water_pumping_station : 1 : Scheduled_delivery_R1_pressure |  |  | Scheduled Delivery Window 1 Pressure Setpoint | Analog Control | mAHD | [7 empty] | Setpoint | 15510 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
48 | stn1dcSchDelR2En | Water_pumping_station | 1 | Scheduled_delivery_R2_enable | Water_pumping_station : 1 : Scheduled_delivery_R2_enable | No | Yes | Scheduled Delivery Window 2 Enabled | Digital Control | [8 empty] | Setpoint | 10503 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
49 | stn1acSchDelR2St | Water_pumping_station | 1 | Scheduled_delivery_R2_start_time | Water_pumping_station : 1 : Scheduled_delivery_R2_start_time |  |  | Scheduled Delivery Window 2 Start Time | Analog Control | Time | [7 empty] | Setpoint | 10507 | DINT | VarInput | g30v2 16bit Analog In | Class 0 | Static | None | None
50 | stn1acSchDelR2Pre | Water_pumping_station | 1 | Scheduled_delivery_R2_pressure | Water_pumping_station : 1 : Scheduled_delivery_R2_pressure |  |  | Scheduled Delivery Window 2 Pressure Setpoint | Analog Control | mAHD | [7 empty] | Setpoint | 15511 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
51 | stn1dcSchDelR3En | Water_pumping_station | 1 | Scheduled_delivery_R3_enable | Water_pumping_station : 1 : Scheduled_delivery_R3_enable | No | Yes | Scheduled Delivery Window 3 Enabled | Digital Control | [8 empty] | Setpoint | 10504 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
52 | stn1acSchDelR3St | Water_pumping_station | 1 | Scheduled_delivery_R3_start_time | Water_pumping_station : 1 : Scheduled_delivery_R3_start_time |  |  | Scheduled Delivery Window 3 Start Time | Analog Control | Time | [7 empty] | Setpoint | 10508 | DINT | VarInput | g30v2 16bit Analog In | Class 0 | Static | None | None
53 | stn1acSchDelR3Pre | Water_pumping_station | 1 | Scheduled_delivery_R3_pressure | Water_pumping_station : 1 : Scheduled_delivery_R3_pressure |  |  | Scheduled Delivery Window 3 Pressure Setpoint | Analog Control | mAHD | [7 empty] | Setpoint | 15512 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
54 | stn1dcSchDelR4En | Water_pumping_station | 1 | Scheduled_delivery_R4_enable | Water_pumping_station : 1 : Scheduled_delivery_R4_enable | No | Yes | Scheduled Delivery Window 4 Enabled | Digital Control | [8 empty] | Setpoint | 10505 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
55 | stn1acSchDelR4St | Water_pumping_station | 1 | Scheduled_delivery_R4_start_time | Water_pumping_station : 1 : Scheduled_delivery_R4_start_time |  |  | Scheduled Delivery Window 4 Start Time | Analog Control | Time | [7 empty] | Setpoint | 10509 | DINT | VarInput | g30v2 16bit Analog In | Class 0 | Static | None | None
56 | stn1acSchDelR4Pre | Water_pumping_station | 1 | Scheduled_delivery_R4_pressure | Water_pumping_station : 1 : Scheduled_delivery_R4_pressure |  |  | Scheduled Delivery Window 4 Pressure Setpoint | Analog Control | mAHD | [7 empty] | Setpoint | 15513 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
57 | stn1asSchDelR0PreFbk | Water_pumping_station | 1 | Scheduled_delivery_R0_pressure_Fbk | Water_pumping_station : 1 : Scheduled_delivery_R0_pressure_Fbk |  |  | Scheduled Delivery Window 0 Pressure Setpoint Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15046 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
58 | stn1asSchDelR1StFbk | Water_pumping_station | 1 | Scheduled_delivery_R1_start_time_Fbk | Water_pumping_station : 1 : Scheduled_delivery_R1_start_time_Fbk |  |  | Scheduled Delivery Window 1 Start Time Feedback | Analog Status | Time |  |  | Y | Y |  |  |  | Setpoint Feedback | 10044 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
59 | stn1asSchDelR1PreFbk | Water_pumping_station | 1 | Scheduled_delivery_R1_pressure_Fbk | Water_pumping_station : 1 : Scheduled_delivery_R1_pressure_Fbk |  |  | Scheduled Delivery Window 1 Pressure Setpoint Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15047 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
60 | stn1dsSchDelR2EnFbk | Water_pumping_station | 1 | Scheduled_delivery_R2_enable_Fbk | Water_pumping_station : 1 : Scheduled_delivery_R2_enable_Fbk | No | Yes | Scheduled Delivery Window 2 Enabled Feedback | Digital Status |  | Event | Y | [5 empty] | Setpoint Feedback | 10022 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
61 | stn1asSchDelR2StFbk | Water_pumping_station | 1 | Scheduled_delivery_R2_start_time_Fbk | Water_pumping_station : 1 : Scheduled_delivery_R2_start_time_Fbk |  |  | Scheduled Delivery Window 2 Start Time Feedback | Analog Status | Time |  |  | Y | Y |  |  |  | Setpoint Feedback | 10045 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
62 | stn1asSchDelR2PreFbk | Water_pumping_station | 1 | Scheduled_delivery_R2_pressure_Fbk | Water_pumping_station : 1 : Scheduled_delivery_R2_pressure_Fbk |  |  | Scheduled Delivery Window 2 Pressure Setpoint Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15048 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
63 | stn1dsSchDelR3EnFbk | Water_pumping_station | 1 | Scheduled_delivery_R3_enable_Fbk | Water_pumping_station : 1 : Scheduled_delivery_R3_enable_Fbk | No | Yes | Scheduled Delivery Window 3 Enabled Feedback | Digital Status |  | Event | Y | [5 empty] | Setpoint Feedback | 10023 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
64 | stn1asSchDelR3StFbk | Water_pumping_station | 1 | Scheduled_delivery_R3_start_time_Fbk | Water_pumping_station : 1 : Scheduled_delivery_R3_start_time_Fbk |  |  | Scheduled Delivery Window 3 Start Time Feedback | Analog Status | Time |  |  | Y | Y |  |  |  | Setpoint Feedback | 10046 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
65 | stn1asSchDelR3PreFbk | Water_pumping_station | 1 | Scheduled_delivery_R3_pressure_Fbk | Water_pumping_station : 1 : Scheduled_delivery_R3_pressure_Fbk |  |  | Scheduled Delivery Window 3 Pressure Setpoint Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15049 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
66 | stn1dsSchDelR4EnFbk | Water_pumping_station | 1 | Scheduled_delivery_R4_enable_Fbk | Water_pumping_station : 1 : Scheduled_delivery_R4_enable_Fbk | No | Yes | Scheduled Delivery Window 4 Enabled Feedback | Digital Status |  | Event | Y | [5 empty] | Setpoint Feedback | 10024 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
67 | stn1asSchDelR4StFbk | Water_pumping_station | 1 | Scheduled_delivery_R4_start_time_Fbk | Water_pumping_station : 1 : Scheduled_delivery_R4_start_time_Fbk |  |  | Scheduled Delivery Window 4 Start Time Feedback | Analog Status | Time |  |  | Y | Y |  |  |  | Setpoint Feedback | 10047 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
68 | stn1asSchDelR4PreFbk | Water_pumping_station | 1 | Scheduled_delivery_R4_pressure_Fbk | Water_pumping_station : 1 : Scheduled_delivery_R4_pressure_Fbk |  |  | Scheduled Delivery Window 4 Pressure Setpoint Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15050 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
69 | stn1asSchDelModeRPS3 | Water_pumping_station | 1 | Scheduled_delivery_required_pressure_setpoint | Water_pumping_station : 1 : Scheduled_delivery_required_pressure_setpoint |  |  | Scheduled Delivery Mode Required Pressure Setpoint (RPS3) | Analog Status | mAHD |  |  | Y | Y |  |  |  | Calculation | 15045 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
70 | stn1prSchDelR0PreDef | Water_pumping_station | 1 | Scheduled_delivery_R0_pressure_default | Water_pumping_station : 1 : Scheduled_delivery_R0_pressure_default |  |  | Scheduled Delivery Window 0 Pressure Setpoint Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15052 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
71 | stn1prSchDelR1StDef | Water_pumping_station | 1 | Scheduled_delivery_R1_start_time_default | Water_pumping_station : 1 : Scheduled_delivery_R1_start_time_default |  |  | Scheduled Delivery Window 1 Start Time Default | Analog Status | Time | [6 empty] | Y | Parameter Feedback | 10052 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
72 | stn1prSchDelR1PreDef | Water_pumping_station | 1 | Scheduled_delivery_R1_pressure_default | Water_pumping_station : 1 : Scheduled_delivery_R1_pressure_default |  |  | Scheduled Delivery Window 1 Pressure Setpoint Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15053 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
73 | stn1pbSchDelR2EnDef | Water_pumping_station | 1 | Scheduled_delivery_R2_enable_default | Water_pumping_station : 1 : Scheduled_delivery_R2_enable_default | No | Yes | Scheduled Delivery Window 2 Enabled Default | Digital Status | [7 empty] | Y | Parameter Feedback | 10025 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
74 | stn1prSchDelR2StDef | Water_pumping_station | 1 | Scheduled_delivery_R2_start_time_default | Water_pumping_station : 1 : Scheduled_delivery_R2_start_time_default |  |  | Scheduled Delivery Window 2 Start Time Default | Analog Status | Time | [6 empty] | Y | Parameter Feedback | 10053 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
75 | stn1prSchDelR2PreDef | Water_pumping_station | 1 | Scheduled_delivery_R2_pressure_default | Water_pumping_station : 1 : Scheduled_delivery_R2_pressure_default |  |  | Scheduled Delivery Window 2 Pressure Setpoint Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15054 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
76 | stn1pbSchDelR3EnDef | Water_pumping_station | 1 | Scheduled_delivery_R3_enable_default | Water_pumping_station : 1 : Scheduled_delivery_R3_enable_default | No | Yes | Scheduled Delivery Window 3 Enabled Default | Digital Status | [7 empty] | Y | Parameter Feedback | 10026 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
77 | stn1prSchDelR3StDef | Water_pumping_station | 1 | Scheduled_delivery_R3_start_time_default | Water_pumping_station : 1 : Scheduled_delivery_R3_start_time_default |  |  | Scheduled Delivery Window 3 Start Time Default | Analog Status | Time | [6 empty] | Y | Parameter Feedback | 10054 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
78 | stn1prSchDelR3PreDef | Water_pumping_station | 1 | Scheduled_delivery_R3_pressure_default | Water_pumping_station : 1 : Scheduled_delivery_R3_pressure_default |  |  | Scheduled Delivery Window 3 Pressure Setpoint Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15055 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
79 | stn1pbSchDelR4EnDef | Water_pumping_station | 1 | Scheduled_delivery_R4_enable_default | Water_pumping_station : 1 : Scheduled_delivery_R4_enable_default | No | Yes | Scheduled Delivery Window 4 Enabled Default | Digital Status | [7 empty] | Y | Parameter Feedback | 10027 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
80 | stn1prSchDelR4StDef | Water_pumping_station | 1 | Scheduled_delivery_R4_start_time_default | Water_pumping_station : 1 : Scheduled_delivery_R4_start_time_default |  |  | Scheduled Delivery Window 4 Start Time Default | Analog Status | Time | [6 empty] | Y | Parameter Feedback | 10055 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
81 | stn1prSchDelR4PreDef | Water_pumping_station | 1 | Scheduled_delivery_R4_pressure_default | Water_pumping_station : 1 : Scheduled_delivery_R4_pressure_default |  |  | Scheduled Delivery Window 4 Pressure Setpoint Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15056 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
82 | stn1dsFlwModTabInv | Water_pumping_station | 1 | Flow_modulation_table_invalid | Water_pumping_station : 1 : Flow_modulation_table_invalid | Ok | Fault | Flow Mode Lookup Table Invalid | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10031 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
83 | stn1prFlwModFlwMax | Water_pumping_station | 1 | Flow_modulation_flow_max | Water_pumping_station : 1 : Flow_modulation_flow_max |  |  | Flow Modulation Mode Maximum Flow | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15150 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
84 | stn1prFlwModFlwMin | Water_pumping_station | 1 | Flow_modulation_flow_min | Water_pumping_station : 1 : Flow_modulation_flow_min |  |  | Flow Modulation Mode Minimum Flow | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15151 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
85 | stn1prFlwModHysMax | Water_pumping_station | 1 | Flow_modulation_hysteresis_max | Water_pumping_station : 1 : Flow_modulation_hysteresis_max |  |  | Flow Modulation Mode Maximum Hysteresis | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15148 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
86 | stn1prFlwModHysMin | Water_pumping_station | 1 | Flow_modulation_hysteresis_min | Water_pumping_station : 1 : Flow_modulation_hysteresis_min |  |  | Flow Modulation Mode Minimum Hysteresis | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15149 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
87 | stn1prFlwModHysDlyMax | Water_pumping_station | 1 | Flow_modulation_hysteresis_delay_max | Water_pumping_station : 1 : Flow_modulation_hysteresis_delay_max |  |  | Flow Modulation Mode Maximum Hysteresis Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10049 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
88 | stn1prFlwModHysDlyMin | Water_pumping_station | 1 | Flow_modulation_hysteresis_delay_min | Water_pumping_station : 1 : Flow_modulation_hysteresis_delay_min |  |  | Flow Modulation Mode Minimum Hysteresis Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10050 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
89 | stn1dcFlwModR2En | Water_pumping_station | 1 | Flow_modulation_R2_enable | Water_pumping_station : 1 : Flow_modulation_R2_enable | No | Yes | Flow Mode Row 2 Enabled | Digital Control | [8 empty] | Setpoint | 10507 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
90 | stn1dcFlwModR3En | Water_pumping_station | 1 | Flow_modulation_R3_enable | Water_pumping_station : 1 : Flow_modulation_R3_enable | No | Yes | Flow Mode Row 3 Enabled | Digital Control | [8 empty] | Setpoint | 10508 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
91 | stn1dcFlwModR4En | Water_pumping_station | 1 | Flow_modulation_R4_enable | Water_pumping_station : 1 : Flow_modulation_R4_enable | No | Yes | Flow Mode Row 4 Enabled | Digital Control | [8 empty] | Setpoint | 10509 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
92 | stn1dcFlwModR5En | Water_pumping_station | 1 | Flow_modulation_R5_enable | Water_pumping_station : 1 : Flow_modulation_R5_enable | No | Yes | Flow Mode Row 5 Enabled | Digital Control | [8 empty] | Setpoint | 10510 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
93 | stn1dcFlwModR6En | Water_pumping_station | 1 | Flow_modulation_R6_enable | Water_pumping_station : 1 : Flow_modulation_R6_enable | No | Yes | Flow Mode Row 6 Enabled | Digital Control | [8 empty] | Setpoint | 10511 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
94 | stn1dcFlwModR7En | Water_pumping_station | 1 | Flow_modulation_R7_enable | Water_pumping_station : 1 : Flow_modulation_R7_enable | No | Yes | Flow Mode Row 7 Enabled | Digital Control | [8 empty] | Setpoint | 10512 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
95 | stn1acFlwModR1Flw | Water_pumping_station | 1 | Flow_modulation_R1_flow | Water_pumping_station : 1 : Flow_modulation_R1_flow |  |  | Flow Mode Flow Rate X1 | Analog Control | L/s | [7 empty] | Setpoint | 15522 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
96 | stn1acFlwModR2Flw | Water_pumping_station | 1 | Flow_modulation_R2_flow | Water_pumping_station : 1 : Flow_modulation_R2_flow |  |  | Flow Mode Flow Rate X2 | Analog Control | L/s | [7 empty] | Setpoint | 15523 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
97 | stn1acFlwModR3Flw | Water_pumping_station | 1 | Flow_modulation_R3_flow | Water_pumping_station : 1 : Flow_modulation_R3_flow |  |  | Flow Mode Flow Rate X3 | Analog Control | L/s | [7 empty] | Setpoint | 15524 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
98 | stn1acFlwModR4Flw | Water_pumping_station | 1 | Flow_modulation_R4_flow | Water_pumping_station : 1 : Flow_modulation_R4_flow |  |  | Flow Mode Flow Rate X4 | Analog Control | L/s | [7 empty] | Setpoint | 15525 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
99 | stn1acFlwModR5Flw | Water_pumping_station | 1 | Flow_modulation_R5_flow | Water_pumping_station : 1 : Flow_modulation_R5_flow |  |  | Flow Mode Flow Rate X5 | Analog Control | L/s | [7 empty] | Setpoint | 15526 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
100 | stn1acFlwModR6Flw | Water_pumping_station | 1 | Flow_modulation_R6_flow | Water_pumping_station : 1 : Flow_modulation_R6_flow |  |  | Flow Mode Flow Rate X6 | Analog Control | L/s | [7 empty] | Setpoint | 15527 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
101 | stn1acFlwModR7Flw | Water_pumping_station | 1 | Flow_modulation_R7_flow | Water_pumping_station : 1 : Flow_modulation_R7_flow |  |  | Flow Mode Flow Rate X7 | Analog Control | L/s | [7 empty] | Setpoint | 15528 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
102 | stn1acFlwModR0Pre | Water_pumping_station | 1 | Flow_modulation_R0_pressure | Water_pumping_station : 1 : Flow_modulation_R0_pressure |  |  | Flow Mode Pressure Setpoint Y0 | Analog Control | mAHD | [7 empty] | Setpoint | 15529 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
103 | stn1acFlwModR1Pre | Water_pumping_station | 1 | Flow_modulation_R1_pressure | Water_pumping_station : 1 : Flow_modulation_R1_pressure |  |  | Flow Mode Pressure Setpoint Y1 | Analog Control | mAHD | [7 empty] | Setpoint | 15530 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
104 | stn1acFlwModR2Pre | Water_pumping_station | 1 | Flow_modulation_R2_pressure | Water_pumping_station : 1 : Flow_modulation_R2_pressure |  |  | Flow Mode Pressure Setpoint Y2 | Analog Control | mAHD | [7 empty] | Setpoint | 15531 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
105 | stn1acFlwModR3Pre | Water_pumping_station | 1 | Flow_modulation_R3_pressure | Water_pumping_station : 1 : Flow_modulation_R3_pressure |  |  | Flow Mode Pressure Setpoint Y3 | Analog Control | mAHD | [7 empty] | Setpoint | 15532 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
106 | stn1acFlwModR4Pre | Water_pumping_station | 1 | Flow_modulation_R4_pressure | Water_pumping_station : 1 : Flow_modulation_R4_pressure |  |  | Flow Mode Pressure Setpoint Y4 | Analog Control | mAHD | [7 empty] | Setpoint | 15533 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
107 | stn1acFlwModR5Pre | Water_pumping_station | 1 | Flow_modulation_R5_pressure | Water_pumping_station : 1 : Flow_modulation_R5_pressure |  |  | Flow Mode Pressure Setpoint Y5 | Analog Control | mAHD | [7 empty] | Setpoint | 15534 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
108 | stn1acFlwModR6Pre | Water_pumping_station | 1 | Flow_modulation_R6_pressure | Water_pumping_station : 1 : Flow_modulation_R6_pressure |  |  | Flow Mode Pressure Setpoint Y6 | Analog Control | mAHD | [7 empty] | Setpoint | 15535 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
109 | stn1acFlwModR7Pre | Water_pumping_station | 1 | Flow_modulation_R7_pressure | Water_pumping_station : 1 : Flow_modulation_R7_pressure |  |  | Flow Mode Pressure Setpoint Y7 | Analog Control | mAHD | [7 empty] | Setpoint | 15536 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
110 | stn1acFlwModR1Hys | Water_pumping_station | 1 | Flow_modulation_R1_hysteresis | Water_pumping_station : 1 : Flow_modulation_R1_hysteresis |  |  | Flow Mode Flow Hysteresis H1 | Analog Control | L/s | [7 empty] | Setpoint | 15515 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
111 | stn1acFlwModR2Hys | Water_pumping_station | 1 | Flow_modulation_R2_hysteresis | Water_pumping_station : 1 : Flow_modulation_R2_hysteresis |  |  | Flow Mode Flow Hysteresis H2 | Analog Control | L/s | [7 empty] | Setpoint | 15516 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
112 | stn1acFlwModR3Hys | Water_pumping_station | 1 | Flow_modulation_R3_hysteresis | Water_pumping_station : 1 : Flow_modulation_R3_hysteresis |  |  | Flow Mode Flow Hysteresis H3 | Analog Control | L/s | [7 empty] | Setpoint | 15517 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
113 | stn1acFlwModR4Hys | Water_pumping_station | 1 | Flow_modulation_R4_hysteresis | Water_pumping_station : 1 : Flow_modulation_R4_hysteresis |  |  | Flow Mode Flow Hysteresis H4 | Analog Control | L/s | [7 empty] | Setpoint | 15518 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
114 | stn1acFlwModR5Hys | Water_pumping_station | 1 | Flow_modulation_R5_hysteresis | Water_pumping_station : 1 : Flow_modulation_R5_hysteresis |  |  | Flow Mode Flow Hysteresis H5 | Analog Control | L/s | [7 empty] | Setpoint | 15519 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
115 | stn1acFlwModR6Hys | Water_pumping_station | 1 | Flow_modulation_R6_hysteresis | Water_pumping_station : 1 : Flow_modulation_R6_hysteresis |  |  | Flow Mode Flow Hysteresis H6 | Analog Control | L/s | [7 empty] | Setpoint | 15520 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
116 | stn1acFlwModR7Hys | Water_pumping_station | 1 | Flow_modulation_R7_hysteresis | Water_pumping_station : 1 : Flow_modulation_R7_hysteresis |  |  | Flow Mode Flow Hysteresis H7 | Analog Control | L/s | [7 empty] | Setpoint | 15521 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
117 | stn1acFlwModR1HysDly | Water_pumping_station | 1 | Flow_modulation_R1_hysteresis_delay | Water_pumping_station : 1 : Flow_modulation_R1_hysteresis_delay |  |  | Flow Mode Hysteresis Delay D1 | Analog Control | s | [7 empty] | Setpoint | 10511 | DINT | VarInput | g30v2 16bit Analog In | Class 0 | Static | None | None
118 | stn1acFlwModR2HysDly | Water_pumping_station | 1 | Flow_modulation_R2_hysteresis_delay | Water_pumping_station : 1 : Flow_modulation_R2_hysteresis_delay |  |  | Flow Mode Hysteresis Delay D2 | Analog Control | s | [7 empty] | Setpoint | 10512 | DINT | VarInput | g30v2 16bit Analog In | Class 0 | Static | None | None
119 | stn1acFlwModR3HysDly | Water_pumping_station | 1 | Flow_modulation_R3_hysteresis_delay | Water_pumping_station : 1 : Flow_modulation_R3_hysteresis_delay |  |  | Flow Mode Hysteresis Delay D3 | Analog Control | s | [7 empty] | Setpoint | 10513 | DINT | VarInput | g30v2 16bit Analog In | Class 0 | Static | None | None
120 | stn1acFlwModR4HysDly | Water_pumping_station | 1 | Flow_modulation_R4_hysteresis_delay | Water_pumping_station : 1 : Flow_modulation_R4_hysteresis_delay |  |  | Flow Mode Hysteresis Delay D4 | Analog Control | s | [7 empty] | Setpoint | 10514 | DINT | VarInput | g30v2 16bit Analog In | Class 0 | Static | None | None
121 | stn1acFlwModR5HysDly | Water_pumping_station | 1 | Flow_modulation_R5_hysteresis_delay | Water_pumping_station : 1 : Flow_modulation_R5_hysteresis_delay |  |  | Flow Mode Hysteresis Delay D5 | Analog Control | s | [7 empty] | Setpoint | 10515 | DINT | VarInput | g30v2 16bit Analog In | Class 0 | Static | None | None
122 | stn1acFlwModR6HysDly | Water_pumping_station | 1 | Flow_modulation_R6_hysteresis_delay | Water_pumping_station : 1 : Flow_modulation_R6_hysteresis_delay |  |  | Flow Mode Hysteresis Delay D6 | Analog Control | s | [7 empty] | Setpoint | 10516 | DINT | VarInput | g30v2 16bit Analog In | Class 0 | Static | None | None
123 | stn1acFlwModR7HysDly | Water_pumping_station | 1 | Flow_modulation_R7_hysteresis_delay | Water_pumping_station : 1 : Flow_modulation_R7_hysteresis_delay |  |  | Flow Mode Hysteresis Delay D7 | Analog Control | s | [7 empty] | Setpoint | 10517 | DINT | VarInput | g30v2 16bit Analog In | Class 0 | Static | None | None
124 | stn1dsFlwModR2EnFbk | Water_pumping_station | 1 | Flow_modulation_R2_enable_Fbk | Water_pumping_station : 1 : Flow_modulation_R2_enable_Fbk | No | Yes | Flow Mode Row 2 Enabled Feedback | Digital Status |  | Event | Y | [5 empty] | Setpoint Feedback | 10033 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
125 | stn1dsFlwModR3EnFbk | Water_pumping_station | 1 | Flow_modulation_R3_enable_Fbk | Water_pumping_station : 1 : Flow_modulation_R3_enable_Fbk | No | Yes | Flow Mode Row 3 Enabled Feedback | Digital Status |  | Event | Y | [5 empty] | Setpoint Feedback | 10034 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
126 | stn1dsFlwModR4EnFbk | Water_pumping_station | 1 | Flow_modulation_R4_enable_Fbk | Water_pumping_station : 1 : Flow_modulation_R4_enable_Fbk | No | Yes | Flow Mode Row 4 Enabled Feedback | Digital Status |  | Event | Y | [5 empty] | Setpoint Feedback | 10035 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
127 | stn1dsFlwModR5EnFbk | Water_pumping_station | 1 | Flow_modulation_R5_enable_Fbk | Water_pumping_station : 1 : Flow_modulation_R5_enable_Fbk | No | Yes | Flow Mode Row 5 Enabled Feedback | Digital Status |  | Event | Y | [5 empty] | Setpoint Feedback | 10036 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
128 | stn1dsFlwModR6EnFbk | Water_pumping_station | 1 | Flow_modulation_R6_enable_Fbk | Water_pumping_station : 1 : Flow_modulation_R6_enable_Fbk | No | Yes | Flow Mode Row 6 Enabled Feedback | Digital Status |  | Event | Y | [5 empty] | Setpoint Feedback | 10037 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
129 | stn1dsFlwModR7EnFbk | Water_pumping_station | 1 | Flow_modulation_R7_enable_Fbk | Water_pumping_station : 1 : Flow_modulation_R7_enable_Fbk | No | Yes | Flow Mode Row 7 Enabled Feedback | Digital Status |  | Event | Y | [5 empty] | Setpoint Feedback | 10038 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
130 | stn1asFlwModR1FlwFbk | Water_pumping_station | 1 | Flow_modulation_R1_flow_Fbk | Water_pumping_station : 1 : Flow_modulation_R1_flow_Fbk |  |  | Flow Mode Flow Rate X1 Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15109 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
131 | stn1asFlwModR2FlwFbk | Water_pumping_station | 1 | Flow_modulation_R2_flow_Fbk | Water_pumping_station : 1 : Flow_modulation_R2_flow_Fbk |  |  | Flow Mode Flow Rate X2 Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15110 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
132 | stn1asFlwModR3FlwFbk | Water_pumping_station | 1 | Flow_modulation_R3_flow_Fbk | Water_pumping_station : 1 : Flow_modulation_R3_flow_Fbk |  |  | Flow Mode Flow Rate X3 Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15111 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
133 | stn1asFlwModR4FlwFbk | Water_pumping_station | 1 | Flow_modulation_R4_flow_Fbk | Water_pumping_station : 1 : Flow_modulation_R4_flow_Fbk |  |  | Flow Mode Flow Rate X4 Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15112 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
134 | stn1asFlwModR5FlwFbk | Water_pumping_station | 1 | Flow_modulation_R5_flow_Fbk | Water_pumping_station : 1 : Flow_modulation_R5_flow_Fbk |  |  | Flow Mode Flow Rate X5 Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15113 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
135 | stn1asFlwModR6FlwFbk | Water_pumping_station | 1 | Flow_modulation_R6_flow_Fbk | Water_pumping_station : 1 : Flow_modulation_R6_flow_Fbk |  |  | Flow Mode Flow Rate X6 Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15114 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
136 | stn1asFlwModR7FlwFbk | Water_pumping_station | 1 | Flow_modulation_R7_flow_Fbk | Water_pumping_station : 1 : Flow_modulation_R7_flow_Fbk |  |  | Flow Mode Flow Rate X7 Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15115 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
137 | stn1asFlwModR0PreFbk | Water_pumping_station | 1 | Flow_modulation_R0_pressure_Fbk | Water_pumping_station : 1 : Flow_modulation_R0_pressure_Fbk |  |  | Flow Mode Pressure Setpoint Y0 Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15116 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
138 | stn1asFlwModR1PreFbk | Water_pumping_station | 1 | Flow_modulation_R1_pressure_Fbk | Water_pumping_station : 1 : Flow_modulation_R1_pressure_Fbk |  |  | Flow Mode Pressure Setpoint Y1 Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15117 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
139 | stn1asFlwModR2PreFbk | Water_pumping_station | 1 | Flow_modulation_R2_pressure_Fbk | Water_pumping_station : 1 : Flow_modulation_R2_pressure_Fbk |  |  | Flow Mode Pressure Setpoint Y2 Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15118 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
140 | stn1asFlwModR3PreFbk | Water_pumping_station | 1 | Flow_modulation_R3_pressure_Fbk | Water_pumping_station : 1 : Flow_modulation_R3_pressure_Fbk |  |  | Flow Mode Pressure Setpoint Y3 Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15119 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
141 | stn1asFlwModR4PreFbk | Water_pumping_station | 1 | Flow_modulation_R4_pressure_Fbk | Water_pumping_station : 1 : Flow_modulation_R4_pressure_Fbk |  |  | Flow Mode Pressure Setpoint Y4 Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15120 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
142 | stn1asFlwModR5PreFbk | Water_pumping_station | 1 | Flow_modulation_R5_pressure_Fbk | Water_pumping_station : 1 : Flow_modulation_R5_pressure_Fbk |  |  | Flow Mode Pressure Setpoint Y5 Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15121 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
143 | stn1asFlwModR6PreFbk | Water_pumping_station | 1 | Flow_modulation_R6_pressure_Fbk | Water_pumping_station : 1 : Flow_modulation_R6_pressure_Fbk |  |  | Flow Mode Pressure Setpoint Y6 Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15122 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
144 | stn1asFlwModR7PreFbk | Water_pumping_station | 1 | Flow_modulation_R7_pressure_Fbk | Water_pumping_station : 1 : Flow_modulation_R7_pressure_Fbk |  |  | Flow Mode Pressure Setpoint Y7 Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15123 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
145 | stn1asFlwModR1HysFbk | Water_pumping_station | 1 | Flow_modulation_R1_hysteresis_Fbk | Water_pumping_station : 1 : Flow_modulation_R1_hysteresis_Fbk |  |  | Flow Mode Flow Hysteresis H1 Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15102 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
146 | stn1asFlwModR2HysFbk | Water_pumping_station | 1 | Flow_modulation_R2_hysteresis_Fbk | Water_pumping_station : 1 : Flow_modulation_R2_hysteresis_Fbk |  |  | Flow Mode Flow Hysteresis H2 Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15103 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
147 | stn1asFlwModR3HysFbk | Water_pumping_station | 1 | Flow_modulation_R3_hysteresis_Fbk | Water_pumping_station : 1 : Flow_modulation_R3_hysteresis_Fbk |  |  | Flow Mode Flow Hysteresis H3 Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15104 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
148 | stn1asFlwModR4HysFbk | Water_pumping_station | 1 | Flow_modulation_R4_hysteresis_Fbk | Water_pumping_station : 1 : Flow_modulation_R4_hysteresis_Fbk |  |  | Flow Mode Flow Hysteresis H4 Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15105 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
149 | stn1asFlwModR5HysFbk | Water_pumping_station | 1 | Flow_modulation_R5_hysteresis_Fbk | Water_pumping_station : 1 : Flow_modulation_R5_hysteresis_Fbk |  |  | Flow Mode Flow Hysteresis H5 Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15106 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
150 | stn1asFlwModR6HysFbk | Water_pumping_station | 1 | Flow_modulation_R6_hysteresis_Fbk | Water_pumping_station : 1 : Flow_modulation_R6_hysteresis_Fbk |  |  | Flow Mode Flow Hysteresis H6 Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15107 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
151 | stn1asFlwModR7HysFbk | Water_pumping_station | 1 | Flow_modulation_R7_hysteresis_Fbk | Water_pumping_station : 1 : Flow_modulation_R7_hysteresis_Fbk |  |  | Flow Mode Flow Hysteresis H7 Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15108 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
152 | stn1asFlwModR1HysDlyFbk | Water_pumping_station | 1 | Flow_modulation_R1_hysteresis_delay_Fbk | Water_pumping_station : 1 : Flow_modulation_R1_hysteresis_delay_Fbk |  |  | Flow Mode Hysteresis Delay D1 Feedback | Analog Status | s |  |  | Y | Y |  |  |  | Setpoint Feedback | 10057 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
153 | stn1asFlwModR2HysDlyFbk | Water_pumping_station | 1 | Flow_modulation_R2_hysteresis_delay_Fbk | Water_pumping_station : 1 : Flow_modulation_R2_hysteresis_delay_Fbk |  |  | Flow Mode Hysteresis Delay D2 Feedback | Analog Status | s |  |  | Y | Y |  |  |  | Setpoint Feedback | 10058 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
154 | stn1asFlwModR3HysDlyFbk | Water_pumping_station | 1 | Flow_modulation_R3_hysteresis_delay_Fbk | Water_pumping_station : 1 : Flow_modulation_R3_hysteresis_delay_Fbk |  |  | Flow Mode Hysteresis Delay D3 Feedback | Analog Status | s |  |  | Y | Y |  |  |  | Setpoint Feedback | 10059 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
155 | stn1asFlwModR4HysDlyFbk | Water_pumping_station | 1 | Flow_modulation_R4_hysteresis_delay_Fbk | Water_pumping_station : 1 : Flow_modulation_R4_hysteresis_delay_Fbk |  |  | Flow Mode Hysteresis Delay D4 Feedback | Analog Status | s |  |  | Y | Y |  |  |  | Setpoint Feedback | 10060 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
156 | stn1asFlwModR5HysDlyFbk | Water_pumping_station | 1 | Flow_modulation_R5_hysteresis_delay_Fbk | Water_pumping_station : 1 : Flow_modulation_R5_hysteresis_delay_Fbk |  |  | Flow Mode Hysteresis Delay D5 Feedback | Analog Status | s |  |  | Y | Y |  |  |  | Setpoint Feedback | 10061 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
157 | stn1asFlwModR6HysDlyFbk | Water_pumping_station | 1 | Flow_modulation_R6_hysteresis_delay_Fbk | Water_pumping_station : 1 : Flow_modulation_R6_hysteresis_delay_Fbk |  |  | Flow Mode Hysteresis Delay D6 Feedback | Analog Status | s |  |  | Y | Y |  |  |  | Setpoint Feedback | 10062 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
158 | stn1asFlwModR7HysDlyFbk | Water_pumping_station | 1 | Flow_modulation_R7_hysteresis_delay_Fbk | Water_pumping_station : 1 : Flow_modulation_R7_hysteresis_delay_Fbk |  |  | Flow Mode Hysteresis Delay D7 Feedback | Analog Status | s |  |  | Y | Y |  |  |  | Setpoint Feedback | 10063 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
159 | stn1asFlwModModeRPS4 | Water_pumping_station | 1 | Flow_modulation_required_pressure_setpoint | Water_pumping_station : 1 : Flow_modulation_required_pressure_setpoint |  |  | Flow Modulation Mode Required Pressure Setpoint (RPS4) | Analog Status | mAHD |  |  | Y | Y |  |  |  | Calculation | 15100 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
160 | stn1pbFlwModR2EnDef | Water_pumping_station | 1 | Flow_modulation_R2_enable_default | Water_pumping_station : 1 : Flow_modulation_R2_enable_default | No | Yes | Flow Mode Row 2 Enabled Default | Digital Status | [7 empty] | Y | Parameter Feedback | 10040 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
161 | stn1pbFlwModR3EnDef | Water_pumping_station | 1 | Flow_modulation_R3_enable_default | Water_pumping_station : 1 : Flow_modulation_R3_enable_default | No | Yes | Flow Mode Row 3 Enabled Default | Digital Status | [7 empty] | Y | Parameter Feedback | 10041 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
162 | stn1pbFlwModR4EnDef | Water_pumping_station | 1 | Flow_modulation_R4_enable_default | Water_pumping_station : 1 : Flow_modulation_R4_enable_default | No | Yes | Flow Mode Row 4 Enabled Default | Digital Status | [7 empty] | Y | Parameter Feedback | 10042 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
163 | stn1pbFlwModR5EnDef | Water_pumping_station | 1 | Flow_modulation_R5_enable_default | Water_pumping_station : 1 : Flow_modulation_R5_enable_default | No | Yes | Flow Mode Row 5 Enabled Default | Digital Status | [7 empty] | Y | Parameter Feedback | 10043 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
164 | stn1pbFlwModR6EnDef | Water_pumping_station | 1 | Flow_modulation_R6_enable_default | Water_pumping_station : 1 : Flow_modulation_R6_enable_default | No | Yes | Flow Mode Row 6 Enabled Default | Digital Status | [7 empty] | Y | Parameter Feedback | 10044 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
165 | stn1pbFlwModR7EnDef | Water_pumping_station | 1 | Flow_modulation_R7_enable_default | Water_pumping_station : 1 : Flow_modulation_R7_enable_default | No | Yes | Flow Mode Row 7 Enabled Default | Digital Status | [7 empty] | Y | Parameter Feedback | 10045 | BOOL | VarOutput | g1v1 Binary Input | Class 0 | Static |  |  | 1 | 0
166 | stn1prFlwModR1FlwDef | Water_pumping_station | 1 | Flow_modulation_R1_flow_default | Water_pumping_station : 1 : Flow_modulation_R1_flow_default |  |  | Flow Mode Flow Rate X1 Default | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15132 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
167 | stn1prFlwModR2FlwDef | Water_pumping_station | 1 | Flow_modulation_R2_flow_default | Water_pumping_station : 1 : Flow_modulation_R2_flow_default |  |  | Flow Mode Flow Rate X2 Default | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15133 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
168 | stn1prFlwModR3FlwDef | Water_pumping_station | 1 | Flow_modulation_R3_flow_default | Water_pumping_station : 1 : Flow_modulation_R3_flow_default |  |  | Flow Mode Flow Rate X3 Default | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15134 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
169 | stn1prFlwModR4FlwDef | Water_pumping_station | 1 | Flow_modulation_R4_flow_default | Water_pumping_station : 1 : Flow_modulation_R4_flow_default |  |  | Flow Mode Flow Rate X4 Default | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15135 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
170 | stn1prFlwModR5FlwDef | Water_pumping_station | 1 | Flow_modulation_R5_flow_default | Water_pumping_station : 1 : Flow_modulation_R5_flow_default |  |  | Flow Mode Flow Rate X5 Default | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15136 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
171 | stn1prFlwModR6FlwDef | Water_pumping_station | 1 | Flow_modulation_R6_flow_default | Water_pumping_station : 1 : Flow_modulation_R6_flow_default |  |  | Flow Mode Flow Rate X6 Default | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15137 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
172 | stn1prFlwModR7FlwDef | Water_pumping_station | 1 | Flow_modulation_R7_flow_default | Water_pumping_station : 1 : Flow_modulation_R7_flow_default |  |  | Flow Mode Flow Rate X7 Default | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15138 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
173 | stn1prFlwModR0PreDef | Water_pumping_station | 1 | Flow_modulation_R0_pressure_default | Water_pumping_station : 1 : Flow_modulation_R0_pressure_default |  |  | Flow Mode Pressure Setpoint Y0 Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15139 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
174 | stn1prFlwModR1PreDef | Water_pumping_station | 1 | Flow_modulation_R1_pressure_default | Water_pumping_station : 1 : Flow_modulation_R1_pressure_default |  |  | Flow Mode Pressure Setpoint Y1 Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15140 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
175 | stn1prFlwModR2PreDef | Water_pumping_station | 1 | Flow_modulation_R2_pressure_default | Water_pumping_station : 1 : Flow_modulation_R2_pressure_default |  |  | Flow Mode Pressure Setpoint Y2 Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15141 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
176 | stn1prFlwModR3PreDef | Water_pumping_station | 1 | Flow_modulation_R3_pressure_default | Water_pumping_station : 1 : Flow_modulation_R3_pressure_default |  |  | Flow Mode Pressure Setpoint Y3 Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15142 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
177 | stn1prFlwModR4PreDef | Water_pumping_station | 1 | Flow_modulation_R4_pressure_default | Water_pumping_station : 1 : Flow_modulation_R4_pressure_default |  |  | Flow Mode Pressure Setpoint Y4 Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15143 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
178 | stn1prFlwModR5PreDef | Water_pumping_station | 1 | Flow_modulation_R5_pressure_default | Water_pumping_station : 1 : Flow_modulation_R5_pressure_default |  |  | Flow Mode Pressure Setpoint Y5 Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15144 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
179 | stn1prFlwModR6PreDef | Water_pumping_station | 1 | Flow_modulation_R6_pressure_default | Water_pumping_station : 1 : Flow_modulation_R6_pressure_default |  |  | Flow Mode Pressure Setpoint Y6 Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15145 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
180 | stn1prFlwModR7PreDef | Water_pumping_station | 1 | Flow_modulation_R7_pressure_default | Water_pumping_station : 1 : Flow_modulation_R7_pressure_default |  |  | Flow Mode Pressure Setpoint Y7 Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15146 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
181 | stn1prFlwModR1HysDef | Water_pumping_station | 1 | Flow_modulation_R1_hysteresis_default | Water_pumping_station : 1 : Flow_modulation_R1_hysteresis_default |  |  | Flow Mode Flow Hysteresis H1 Default | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15125 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
182 | stn1prFlwModR2HysDef | Water_pumping_station | 1 | Flow_modulation_R2_hysteresis_default | Water_pumping_station : 1 : Flow_modulation_R2_hysteresis_default |  |  | Flow Mode Flow Hysteresis H2 Default | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15126 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
183 | stn1prFlwModR3HysDef | Water_pumping_station | 1 | Flow_modulation_R3_hysteresis_default | Water_pumping_station : 1 : Flow_modulation_R3_hysteresis_default |  |  | Flow Mode Flow Hysteresis H3 Default | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15127 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
184 | stn1prFlwModR4HysDef | Water_pumping_station | 1 | Flow_modulation_R4_hysteresis_default | Water_pumping_station : 1 : Flow_modulation_R4_hysteresis_default |  |  | Flow Mode Flow Hysteresis H4 Default | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15128 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
185 | stn1prFlwModR5HysDef | Water_pumping_station | 1 | Flow_modulation_R5_hysteresis_default | Water_pumping_station : 1 : Flow_modulation_R5_hysteresis_default |  |  | Flow Mode Flow Hysteresis H5 Default | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15129 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
186 | stn1prFlwModR6HysDef | Water_pumping_station | 1 | Flow_modulation_R6_hysteresis_default | Water_pumping_station : 1 : Flow_modulation_R6_hysteresis_default |  |  | Flow Mode Flow Hysteresis H6 Default | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15130 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
187 | stn1prFlwModR7HysDef | Water_pumping_station | 1 | Flow_modulation_R7_hysteresis_default | Water_pumping_station : 1 : Flow_modulation_R7_hysteresis_default |  |  | Flow Mode Flow Hysteresis H7 Default | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15131 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
188 | stn1prFlwModR1HysDlyDef | Water_pumping_station | 1 | Flow_modulation_R1_hysteresis_delay_default | Water_pumping_station : 1 : Flow_modulation_R1_hysteresis_delay_default |  |  | Flow Mode Hysteresis Delay D1 Default | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10064 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
189 | stn1prFlwModR2HysDlyDef | Water_pumping_station | 1 | Flow_modulation_R2_hysteresis_delay_default | Water_pumping_station : 1 : Flow_modulation_R2_hysteresis_delay_default |  |  | Flow Mode Hysteresis Delay D2 Default | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10065 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
190 | stn1prFlwModR3HysDlyDef | Water_pumping_station | 1 | Flow_modulation_R3_hysteresis_delay_default | Water_pumping_station : 1 : Flow_modulation_R3_hysteresis_delay_default |  |  | Flow Mode Hysteresis Delay D3 Default | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10066 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
191 | stn1prFlwModR4HysDlyDef | Water_pumping_station | 1 | Flow_modulation_R4_hysteresis_delay_default | Water_pumping_station : 1 : Flow_modulation_R4_hysteresis_delay_default |  |  | Flow Mode Hysteresis Delay D4 Default | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10067 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
192 | stn1prFlwModR5HysDlyDef | Water_pumping_station | 1 | Flow_modulation_R5_hysteresis_delay_default | Water_pumping_station : 1 : Flow_modulation_R5_hysteresis_delay_default |  |  | Flow Mode Hysteresis Delay D5 Default | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10068 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
193 | stn1prFlwModR6HysDlyDef | Water_pumping_station | 1 | Flow_modulation_R6_hysteresis_delay_default | Water_pumping_station : 1 : Flow_modulation_R6_hysteresis_delay_default |  |  | Flow Mode Hysteresis Delay D6 Default | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10069 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
194 | stn1prFlwModR7HysDlyDef | Water_pumping_station | 1 | Flow_modulation_R7_hysteresis_delay_default | Water_pumping_station : 1 : Flow_modulation_R7_hysteresis_delay_default |  |  | Flow Mode Hysteresis Delay D7 Default | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10070 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
195 | zne1prPreFireDef | Water_pumping_station | 1 | Discharge_pressure_default_fire | Water_pumping_station : 1 : Discharge_pressure_default_fire |  |  | Zone Default Fire Pressure | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15005 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
196 | stn1acManPerfSP | Water_pumping_station | 1 | Manual_system_performance_setpoint | Water_pumping_station : 1 : Manual_system_performance_setpoint |  |  | Manual System Performance Setpoint | Analog Control | % | [7 empty] | Setpoint | 15538 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
197 | stn1asManPerfSPFbk | Water_pumping_station | 1 | Manual_system_performance_setpoint_Fbk | Water_pumping_station : 1 : Manual_system_performance_setpoint_Fbk |  |  | Manual System Performance Setpoint Feedback | Analog Status | % |  |  | Y | Y |  |  |  | Setpoint Feedback | 15070 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
198 | stn1prFixSpdNormPerf | Water_pumping_station | 1 | Fixed_speed_mode_normal_system_performance | Water_pumping_station : 1 : Fixed_speed_mode_normal_system_performance |  |  | Fixed Speed Normal System Performance % | Analog Status | % | [6 empty] | Y | Parameter Feedback | 15064 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
199 | stn1prManPerfSPMin | Water_pumping_station | 1 | Manual_system_performance_setpoint_minimum | Water_pumping_station : 1 : Manual_system_performance_setpoint_minimum |  |  | Manual Mode System Performance Setpoint Min | Analog Status | % | [6 empty] | Y | Parameter Feedback | 15072 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
200 | stn1prManPerfSPMax | Water_pumping_station | 1 | Manual_system_performance_setpoint_maximum | Water_pumping_station : 1 : Manual_system_performance_setpoint_maximum |  |  | Manual Mode System Performance Setpoint Max | Analog Status | % | [6 empty] | Y | Parameter Feedback | 15071 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
201 | stn1dcRemStart | Water_pumping_station | 1 | Manual_start | Water_pumping_station : 1 : Manual_start | Off | Start | Manual Mode Pump Set Start | Digital Control | [8 empty] | Digital Control | 10517 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
202 | stn1dcRemStop | Water_pumping_station | 1 | Manual_stop | Water_pumping_station : 1 : Manual_stop | Off | Stop | Manual Mode Pump Set Stop | Digital Control | [8 empty] | Digital Control | 10518 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
203 | stn1prFixSpdFireFlwTh | Water_pumping_station | 1 | Fixed_speed_mode_fire_flow_threshold | Water_pumping_station : 1 : Fixed_speed_mode_fire_flow_threshold |  |  | Fixed Speed Mode Fire Flow Threshold | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15063 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
204 | stn1prFixSpdFirePerf | Water_pumping_station | 1 | Fixed_speed_mode_fire_system_performance | Water_pumping_station : 1 : Fixed_speed_mode_fire_system_performance |  |  | Fixed Speed Mode Fire System Performance % | Analog Status | % | [6 empty] | Y | Parameter Feedback | 15065 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
205 | stn1prFixSpdNormPerfOnDly | Water_pumping_station | 1 | Fixed_speed_mode_return_to_normal_sys_perform_delay | Water_pumping_station : 1 : Fixed_speed_mode_return_to_normal_sys_perform_delay |  |  | Fixed Speed Mode Return to Normal System Performance Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10075 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
206 | gen1asGTStep | Generator | 1 | Test_step | Generator : 1 : Test_step |  |  | Generator Test Current Test Step | Analog Status |  |  |  | Y | Y |  |  |  | Analog Status | 10463 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
207 | gen1dcGTStart | Generator | 1 | Test_start | Generator : 1 : Test_start | Off | Start | Generator Start Generator Test | Digital Control | [8 empty] | Digital Control | 10677 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
208 | gen1dcGTStop | Generator | 1 | Test_stop | Generator : 1 : Test_stop | Off | Stop | Generator Stop Generator Test | Digital Control | [8 empty] | Digital Control | 10678 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
209 | gen1dsGTFSummFlt | Generator | 1 | Last_test_failed | Generator : 1 : Last_test_failed | Ok | Fault | Generator Last Test Failed | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10482 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
210 | gen1dsGTFEntryFlt | Generator | 1 | Last_test_failed_entry_fault | Generator : 1 : Last_test_failed_entry_fault | Ok | Fault | Generator Last Test Failed - Test not Started (Entry Conditions not met) | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10471 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
211 | gen1dsGTFGenStartFlt | Generator | 1 | Last_test_failed_generator_failed_to_start_fault | Generator : 1 : Last_test_failed_generator_failed_to_start_fault | Ok | Fault | Generator Last Test Failed - Generator Fail to Start | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10472 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
212 | gen1dsGTFGenStopPrem | Generator | 1 | Last_test_failed_generator_premature_stop_fault | Generator : 1 : Last_test_failed_generator_premature_stop_fault | Ok | Fault | Generator Last Test Failed - Generator Premature Stop | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10479 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
213 | gen1dsGTFTferToGenFlt | Generator | 1 | Last_test_failed_ATS_failed_to_tfer_to_generator_fault | Generator : 1 : Last_test_failed_ATS_failed_to_tfer_to_generator_fault | Ok | Fault | Generator Last Test Failed - ATS fail to switch to generator | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10473 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
214 | gen1dsGTFTferToMainsPrem | Generator | 1 | Last_test_failed_ATS_premature_tfer_to_energex_fault | Generator : 1 : Last_test_failed_ATS_premature_tfer_to_energex_fault | Ok | Fault | Generator Last Test Failed - ATS premature return to Energex | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10480 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
215 | gen1dsGTFMPCUnavail | Generator | 1 | Last_test_failed_MPC_unavailable_fault | Generator : 1 : Last_test_failed_MPC_unavailable_fault | Ok | Fault | Generator Last Test Failed - MPC Not available | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10481 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
216 | gen1dsGTFPmpStartFlt | Generator | 1 | Last_test_failed_pump_failed_to_start_fault | Generator : 1 : Last_test_failed_pump_failed_to_start_fault | Ok | Fault | Generator Last Test Failed - MPC pump fail to run | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10474 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
217 | gen1dsGTFTferToMainsFlt | Generator | 1 | Last_test_failed_ATS_failed_to_tfer_to_energex_fault | Generator : 1 : Last_test_failed_ATS_failed_to_tfer_to_energex_fault | Ok | Fault | Generator Last Test Failed - ATS fail to return to Energex | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10475 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
218 | gen1dsGTFGenStopFlt | Generator | 1 | Last_test_failed_generator_failed_to_stop_fault | Generator : 1 : Last_test_failed_generator_failed_to_stop_fault | Ok | Fault | Generator Last Test Failed - Generator fail to stop | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10476 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
219 | gen1dsGTFStopOperator | Generator | 1 | Last_test_failed_test_stopped_by_operator_fault | Generator : 1 : Last_test_failed_test_stopped_by_operator_fault | Ok | Fault | Generator Last Test Failed - Test Stopped by Operator | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10477 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
219.1 | gen1dsGTFPwrFlt | Generator | 1 | Last_test_failed_generator_power_fault | Generator : 1 : Last_test_failed_generator_power_fault | Ok | Fault | Generator Last Test Failed - Gen Power Fault | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10485 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
220 | gen1dsGTFAborted | Generator | 1 | Last_test_failed_aborted_fault | Generator : 1 : Last_test_failed_aborted_fault | Ok | Fault | Generator Last Test Failed - Other Abort Condition | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10478 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
221 | gen1dsGTActive | Generator | 1 | Test_sequence_active | Generator : 1 : Test_sequence_active | No | Yes | Generator Test Sequence Active | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10470 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
222 |  |  |  |  | : :
223 | gen1dsGenStartFlt | Generator | 1 | Fail_to_run | Generator : 1 : Fail_to_run | Ok | Fault | Generator Failed to Start | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10460 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
224 | gen1dsATSTferGenFlt | Generator | 1 | ATS_failed_to_transfer_to_generator_fault | Generator : 1 : ATS_failed_to_transfer_to_generator_fault | Ok | Fault | ATS Fail to Transfer to Generator | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10461 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
225 | gen1dsATSTferMainsFlt | Generator | 1 | ATS_failed_to_transfer_to_energex_fault | Generator : 1 : ATS_failed_to_transfer_to_energex_fault | Ok | Fault | ATS Fail to Return to Energex | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10462 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
226 | gen1dsGenStopFlt | Generator | 1 | Fail_to_stop | Generator : 1 : Fail_to_stop | Ok | Fault | Generator Fail to Stop | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10463 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
227 | gen1dsExercise | Generator | 1 | Exercise_relay_active | Generator : 1 : Exercise_relay_active | No | Yes | Generator Exercise Relay Active | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10483 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
228 | gen1dsPmpInhbt | Generator | 1 | Generator_pumps_inhibit_active | Generator : 1 : Generator_pumps_inhibit_active | No | Yes | Generator Pump Inhibit | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10469 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
229 | stn1dsSuppAuthPwrReturnLockout | Generator | 1 | Energex_lockout_active | Generator : 1 : Energex_lockout_active | No | Yes | ATS Return to Energex Lockout Active | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10484 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
230 | gen1prMainsFailtoGenStartDly | Generator | 1 | Energex_fail_to gen_start_delay | Generator : 1 : Energex_fail_to gen_start_delay |  |  | Delay between Energex fail and Generator Start | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10454 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
231 | gen1prGenRunToATSTferDly | Generator | 1 | Generator_start_to_ATS_tfer_delay | Generator : 1 : Generator_start_to_ATS_tfer_delay |  |  | Delay between Gen start and ATS Transfer to Generator | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10456 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
232 | gen1prGStToPmpRunDly | Generator | 1 | Generator_start_to_pumps_run_delay | Generator : 1 : Generator_start_to_pumps_run_delay |  |  | Delay between Gen start and Pump Run | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10459 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
233 | gen1prMOkToATSTferDly | Generator | 1 | Energex_ok_to_ATS_transfer_delay | Generator : 1 : Energex_ok_to_ATS_transfer_delay |  |  | Delay between Energex Restore and ATS Transfer to Normal | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10455 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
234 | gen1prPmpInhbtPreTferDly | Generator | 1 | Pumps_inhibit_duration_before_ATS_transfer | Generator : 1 : Pumps_inhibit_duration_before_ATS_transfer |  |  | Pre ATS transfer pump inhibit duration | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10457 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
235 | gen1prANToPmpRunDly | Generator | 1 | ATS_normal_to_pumps_run_delay | Generator : 1 : ATS_normal_to_pumps_run_delay |  |  | Delay between ATS return to Norm and Pump Run | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10458 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
236 | gen1prEnergexLockoutWnd | Generator | 1 | Energex_lockout_window | Generator : 1 : Energex_lockout_window |  |  | PFRS locked out if Energex fails within this time after ATS returns to normal | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10466 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
237 | gen1prEnergexLockoutDur | Generator | 1 | Energex_lockout_duration | Generator : 1 : Energex_lockout_duration |  |  | PFSR Lockout duration | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10465 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
238 | gen1prATSNormtoGenStopDly | Generator | 1 | ATS_normal_to_gen_stop_delay | Generator : 1 : ATS_normal_to_gen_stop_delay |  |  | Delay between ATS return to Normal and generator stop | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10453 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
239 | gen1prGTFPmpStartOnDly | Generator | 1 | Generator_test_pump_failed_to_start_fault_delay | Generator : 1 : Generator_test_pump_failed_to_start_fault_delay |  |  | Gen Test Pump Startup Time | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10461 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
240 | gen1prGTGenRunDur | Generator | 1 | Generator_test_generator_run_duration | Generator : 1 : Generator_test_generator_run_duration |  |  | Gen Test Generator Run Time | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10460 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
241 | stn1dsSPClampedAlm | Site | 1 | Setpoint_clamped | Site : 1 : Setpoint_clamped | Ok | Fault | Setpoint Clamped Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10002 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
242 | stn1dcSPClampedAlmRst | Site | 1 | Setpoint_clamped_reset | Site : 1 : Setpoint_clamped_reset | Off | Reset | Setpoint Clamped Alarm Reset | Digital Control |  | Alarm(2) (Control Fail) | [6 empty] | Alarm Reset | 10501 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
243 | mpc1dsAvailable | MPC | 1 | Available | MPC : 1 : Available | Fault | Ok | MPC Available | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10400 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
244 | mpc1dsMBCommsFAlm | MPC | 1 | Comms_fail | MPC : 1 : Comms_fail | Ok | Fault | MPC Comms Fail | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10403 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
245 | mpc1dsFlt | MPC | 1 | Fault | MPC : 1 : Fault | Ok | Fault | MPC Fault | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10401 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
246 | mpc1dsWarning | MPC | 1 | Warning | MPC : 1 : Warning | Ok | Fault | MPC Warning | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10402 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
247 | mpc1dsRemModeActive | MPC | 1 | Local_remote | MPC : 1 : Local_remote | No | Yes | MPC in Remote | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10414 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
248 | mpc1dsOn | MPC | 1 | System_operation | MPC : 1 : System_operation | No | Yes | MPC System On | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10413 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
249 | mpc1dsModeCmdFlt | MPC | 1 | Mode_command_fail_alarm | MPC : 1 : Mode_command_fail_alarm | Ok | Fault | MPC Mode Command Fail Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10404 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
250 | mpc1dsSPMMFlt | MPC | 1 | Setpoint_mismatch_alarm | MPC : 1 : Setpoint_mismatch_alarm | Ok | Fault | MPC Setpoint Mismatch Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10405 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
251 | mpc1dsWShortLvl1 | MPC | 1 | Water_shortage_1 | MPC : 1 : Water_shortage_1 | Ok | Fault | MPC Water Shortage 1 | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10420 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
252 | mpc1dsWShortLvl2 | MPC | 1 | Water_shortage_2 | MPC : 1 : Water_shortage_2 | Ok | Fault | MPC Water Shortage 2 | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10421 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
253 | mpc1dsPreHi | MPC | 1 | Pressure_high | MPC : 1 : Pressure_high | Ok | Fault | MPC Pressure High | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10422 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
254 | mpc1dsPreLo | MPC | 1 | Pressure_low | MPC : 1 : Pressure_low | Ok | Fault | MPC Pressure Low | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10423 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
255 | mpc1dsPreRelief | MPC | 1 | Pressure_relief | MPC : 1 : Pressure_relief | Ok | Fault | MPC Pressure Relief | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10424 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
256 | mpc1dsAllPmpsAlarm | MPC | 1 | All_pumps_alarm | MPC : 1 : All_pumps_alarm | Ok | Fault | MPC All Pumps Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10425 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
257 | mpc1dsExtFlt | MPC | 1 | External_fault | MPC : 1 : External_fault | Ok | Fault | MPC External Fault | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10426 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
258 | mpc1dsDissSensSig | MPC | 1 | Dissimilar_sensor_signals | MPC : 1 : Dissimilar_sensor_signals | Ok | Fault | MPC Dissimilar Sensor Signals | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10427 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
259 | mpc1dsFltSensorPri | MPC | 1 | Primary_sensor_fault | MPC : 1 : Primary_sensor_fault | Ok | Fault | MPC Primary Sensor Fault | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10428 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
260 | mpc1dsFltSensor | MPC | 1 | Sensor_fault | MPC : 1 : Sensor_fault | Ok | Fault | MPC Sensor Fault | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10429 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
261 | mpc1dsPmpCommsFlt | MPC | 1 | Communication_with_pumps_fault | MPC : 1 : Communication_with_pumps_fault | Ok | Fault | MPC Communication with pumps fault | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10440 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
262 | mpc1dsPhaseFlt | MPC | 1 | Phase_failure | MPC : 1 : Phase_failure | Ok | Fault | MPC Phase Failure | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10431 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
263 | mpc1dsPmpUVoltage | MPC | 1 | Pump_undervoltage | MPC : 1 : Pump_undervoltage | Ok | Fault | MPC Pump Undervoltage | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10432 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
264 | mpc1dsPmpOVoltage | MPC | 1 | Pump_overvoltage | MPC : 1 : Pump_overvoltage | Ok | Fault | MPC Pump Overvoltage | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10433 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
265 | mpc1dsPmpOverload | MPC | 1 | Pump_overload | MPC : 1 : Pump_overload | Ok | Fault | MPC Pump Overload | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10434 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
266 | mpc1dsMTempHi | MPC | 1 | Motor_temperature_too_high | MPC : 1 : Motor_temperature_too_high | Ok | Fault | MPC Motor Temperature Too High | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10435 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
267 | mpc1dsFltOther | MPC | 1 | Pump_other_fault | MPC : 1 : Pump_other_fault | Ok | Fault | MPC Pump Other Fault | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10436 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
268 | mpc1dsFltCU352 | MPC | 1 | CU352_internal_fault | MPC : 1 : CU352_internal_fault | Ok | Fault | MPC CU352 Internal Fault | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10437 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
269 | mpc1dsFltIO351 | MPC | 1 | IO351_internal_fault | MPC : 1 : IO351_internal_fault | Ok | Fault | MPC IO351 Internal Fault | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10407 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
270 | mpc1dsVSDReadyFlt | MPC | 1 | VFD_not_ready | MPC : 1 : VFD_not_ready | Ok | Fault | MPC VFD Not Ready | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10439 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
271 | mpc1dsFltEthernet | MPC | 1 | Ethernet_fault | MPC : 1 : Ethernet_fault | Ok | Fault | MPC Ethernet Fault | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10408 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
272 | mpc1dsLim1Excd | MPC | 1 | Limit_1_exceeded | MPC : 1 : Limit_1_exceeded | Ok | Fault | MPC Limit 1 Exceeded | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10409 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
273 | mpc1dsLim2Excd | MPC | 1 | Limit_2_exceeded | MPC : 1 : Limit_2_exceeded | Ok | Fault | MPC Limit 2 Exceeded | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10410 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
274 | mpc1dsPreBuildUp | MPC | 1 | Pressure_build_up_fault | MPC : 1 : Pressure_build_up_fault | Ok | Fault | MPC Pressure build-up fault | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10441 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
275 | mpc1dsPmpDutyRngFlt | MPC | 1 | Pumps_outside_duty_range | MPC : 1 : Pumps_outside_duty_range | Ok | Fault | MPC Pumps outside Duty Range | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10442 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
276 | mpc1dsPmpPilotFlt | MPC | 1 | Pilot_pump_fault | MPC : 1 : Pilot_pump_fault | Ok | Fault | MPC Pilot Pump Fault | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10443 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
277 | mpc1dsCIMFlt | MPC | 1 | Comms_interface_module_fault | MPC : 1 : Comms_interface_module_fault | Ok | Fault | MPC CIM (Comms Interface Module) Fault | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10438 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
278 | mpc1asPreInlet | MPC | 1 | Inlet_pressure | MPC : 1 : Inlet_pressure |  |  | MPC Inlet Pressure | Analog Status | mAHD |  |  | Y | Y | 60 | 1 |  | Analog Status | 15407 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
279 | mpc1asPreOutlet | MPC | 1 | Outlet_pressure | MPC : 1 : Outlet_pressure |  |  | MPC Outlet Pressure | Analog Status | mAHD |  |  | Y | Y | 60 | 1 |  | Analog Status | 15408 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
280 | mpc1dsAllPmpsUnavailable | MPC | 1 | All_pumps_unavailable | MPC : 1 : All_pumps_unavailable | Ok | Fault | All Pumps Unavailable | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10417 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
281 | mpc1dcAlarmReset | MPC | 1 | Alarm_reset | MPC : 1 : Alarm_reset | Off | Reset | MPC Alarm Reset | Digital Control |  | Alarm(2) (Control Fail) | [6 empty] | Digital Control | 10652 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
282 | mpc1prMBCommsFAlmOnDly | MPC | 1 | Communications_fault_delay | MPC : 1 : Communications_fault_delay |  |  | MPC Communications Fault Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10404 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
283 | mpc1asFltDebounceDly | MPC | 1 | Hardwired_fault_delay | MPC : 1 : Hardwired_fault_delay |  |  | MPC controller hardwired fault delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10403 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
284 | mpc1prMMFltOnDly | MPC | 1 | Control_and_setpoint_mismatch_fault_on_delay | MPC : 1 : Control_and_setpoint_mismatch_fault_on_delay |  |  | MPC/RTU Control Mode and Setpoint Mismatch Alarm Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10405 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
285
286 | mpc1dsIntProcessOK | MPC | 1 | Process_interlock_healthy | MPC : 1 : Process_interlock_healthy | No | Yes | MPC Process Interlock Healthy | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10448 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
287 | mpc1asOpMode | MPC | 1 | Operation_mode | MPC : 1 : Operation_mode |  |  | Operation Mode | Analog Status |  | Event (States defined in SCADA) |  | Y | Y |  |  |  | Analog Status | 10410 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
288 | mpc1asCtrlMode | MPC | 1 | Control_mode | MPC : 1 : Control_mode |  |  | Control Mode | Analog Status |  | Event (States defined in SCADA) |  | Y | Y |  |  |  | Analog Status | 10411 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
289 | mpc1asAlarmCode | MPC | 1 | Alarm_code | MPC : 1 : Alarm_code |  |  | MPC Alarm Register | Analog Status |  | Event (States defined in SCADA) |  | Y | Y |  |  |  | Analog Status | 10400 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
290 | mpc1asWarningCode | MPC | 1 | Warning_code | MPC : 1 : Warning_code |  |  | MPC Warning Register | Analog Status |  |  |  | Y | Y |  |  |  | Analog Status | 10401 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
291 | mpc1asSPMAHD | MPC | 1 | Setpoint_mahd | MPC : 1 : Setpoint_mahd |  |  | MPC Setpoint mAHD | Analog Status | mAHD |  |  | Y | Y | 15 | 1 |  | Analog Status | 15400 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
292 | mpc1asSPPc | MPC | 1 | Setpoint_% | MPC : 1 : Setpoint_% |  |  | MPC Setpoint % | Analog Status | % |  |  | Y | Y | 15 | 1 |  | Analog Status | 15401 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
293 | mpc1asSPActMAHD | MPC | 1 | Actual_setpoint_mahd | MPC : 1 : Actual_setpoint_mahd |  |  | MPC Actual Setpoint mAHD | Analog Status | mAHD |  |  | Y | Y | 15 | 1 |  | Analog Status | 15402 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
294 | mpc1asSPActPc | MPC | 1 | Actual_setpoint_% | MPC : 1 : Actual_setpoint_% |  |  | MPC Actual Setpoint % | Analog Status | % |  |  | Y | Y | 15 | 1 |  | Analog Status | 15403 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
295 | mpc1asRelPerf | MPC | 1 | Relative_performance | MPC : 1 : Relative_performance |  |  | MPC Relative Performance | Analog Status | % |  |  | Y | Y | 60 | 1 |  | Analog Status | 15406 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
296 | pmp1dsAvailable | MPC_pump | 1 | Available | MPC_pump : 1 : Available | Fault | Ok | MPC Pump 1 Available Alarm | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10306 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
297 | pmp1dsRunning | MPC_pump | 1 | Running | MPC_pump : 1 : Running | Stopped | Running | MPC Pump 1 Running | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10305 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
298 | pmp1dsPresent | MPC_pump | 1 | Present | MPC_pump : 1 : Present | No | Yes | MPC Pump 1 Present | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10309 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
299 | pmp1dsFltMPC | MPC_pump | 1 | Fault_mpc | MPC_pump : 1 : Fault_mpc | Ok | Fault | MPC Pump 1 Pump Fault (MPC) | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10312 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
300 | pmp1dsCommsFlt | MPC_pump | 1 | Comms_fail | MPC_pump : 1 : Comms_fail | Ok | Fault | MPC Pump 1 Comms Fault | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10310 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
301 | pmp1dsAutoActive | MPC_pump | 1 | Auto | MPC_pump : 1 : Auto | No | Yes | MPC Pump 1 Auto Mode | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10308 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
302 | pmp1dsRemModeActive | MPC_pump | 1 | Local_remote | MPC_pump : 1 : Local_remote | No | Yes | MPC Pump 1 Access Mode | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10307 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
303 | pmp1dsFltPmp | MPC_pump | 1 | Fault_pump | MPC_pump : 1 : Fault_pump | Ok | Fault | MPC Pump 1 Pump Fault (Pump) | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10311 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
303.1 | pmp1dsVFDHealthy | MPC_pump | 1 | VFD_healthy | MPC_pump : 1 : VFD_healthy | Fault | Healthy | MPC Pump 1 VFD Healthy Hardwired Status | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10313 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
304 | pmp1asAlarmCode | MPC_pump | 1 | Alarm_code | MPC_pump : 1 : Alarm_code |  |  | MPC Pump 1 Pump Alarm Code | Analog Status |  |  |  | Y | Y |  |  |  | Analog Status | 10304 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
305 | pmp1asSpdPc | MPC_pump | 1 | Speed_Fbk | MPC_pump : 1 : Speed_Fbk |  |  | MPC Pump 1 Speed | Analog Status | % |  |  | Y | Y | 60 | 1 |  | Calculation | 15303 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
306 | pmp1asMCurr | MPC_pump | 1 | Motor_current | MPC_pump : 1 : Motor_current |  |  | MPC Pump 1 Current | Analog Status | A |  |  | Y | Y | 60 | 0.1 |  | Calculation | 15301 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
307 | pmp1asMPwr | MPC_pump | 1 | Motor_power | MPC_pump : 1 : Motor_power |  |  | MPC Pump 1 Power | Analog Status | kW |  |  | Y | Y | 60 | 0.1 |  | Calculation | 15302 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
308
309 | pmp1asStartsTdy | MPC_pump | 1 | Number_of_starts | MPC_pump : 1 : Number_of_starts |  |  | MPC Pump 1 Starts Today | Analog Status |  |  |  | Y | Y |  |  |  | Calculation | 10305 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
310 | pmp1asStartsYdy | MPC_pump | 1 | Number_of_starts_yesterday | MPC_pump : 1 : Number_of_starts_yesterday |  |  | MPC Pump 1 Starts Yesterday | Analog Status |  |  |  | Y | Y |  |  |  | Calculation | 10306 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
311 | pmp1asRunHrsTdy | MPC_pump | 1 | Hours_run | MPC_pump : 1 : Hours_run |  |  | MPC Pump 1 Run Hours | Analog Status | Hours |  |  | Y | Y |  |  |  | Calculation | 15305 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0.25 | Absolute | 15 | 0
312 | pmp1asRunHrsYdy | MPC_pump | 1 | Hours_run_yesterday | MPC_pump : 1 : Hours_run_yesterday |  |  | MPC Pump 1 Run Hours Yesterday | Analog Status | Hours |  |  | Y | Y |  |  |  | Calculation | 15306 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
313 | pmp2dsAvailable | MPC_pump | 2 | Available | MPC_pump : 2 : Available | Fault | Ok | MPC Pump 2 Available Alarm | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10326 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
314 | pmp2dsRunning | MPC_pump | 2 | Running | MPC_pump : 2 : Running | Stopped | Running | MPC Pump 2 Running | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10325 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
315 | pmp2dsPresent | MPC_pump | 2 | Present | MPC_pump : 2 : Present | No | Yes | MPC Pump 2 Present | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10329 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
316 | pmp2dsFltMPC | MPC_pump | 2 | Fault_mpc | MPC_pump : 2 : Fault_mpc | Ok | Fault | MPC Pump 2 Pump Fault (MPC) | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10332 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
317 | pmp2dsCommsFlt | MPC_pump | 2 | Comms_fail | MPC_pump : 2 : Comms_fail | Ok | Fault | MPC Pump 2 Comms Fault | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10330 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
318 | pmp2dsAutoActive | MPC_pump | 2 | Auto | MPC_pump : 2 : Auto | No | Yes | MPC Pump 2 Auto Mode | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10328 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
319 | pmp2dsRemModeActive | MPC_pump | 2 | Local_remote | MPC_pump : 2 : Local_remote | No | Yes | MPC Pump 2 Access Mode | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10327 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
320 | pmp2dsFltPmp | MPC_pump | 2 | Fault_pump | MPC_pump : 2 : Fault_pump | Ok | Fault | MPC Pump 2 Pump Fault (Pump) | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10331 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
320.1 | pmp2dsVFDHealthy | MPC_pump | 2 | VFD_healthy | MPC_pump : 2 : VFD_healthy | Fault | Healthy | MPC Pump 2 VFD Healthy Hardwired Status | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10333 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
321 | pmp2asAlarmCode | MPC_pump | 2 | Alarm_code | MPC_pump : 2 : Alarm_code |  |  | MPC Pump 2 Pump Alarm Code | Analog Status |  |  |  | Y | Y |  |  |  | Analog Status | 10324 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
322 | pmp2asSpdPc | MPC_pump | 2 | Speed_Fbk | MPC_pump : 2 : Speed_Fbk |  |  | MPC Pump 2 Speed | Analog Status | % |  |  | Y | Y | 60 | 1 |  | Calculation | 15323 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
323 | pmp2asMCurr | MPC_pump | 2 | Motor_current | MPC_pump : 2 : Motor_current |  |  | MPC Pump 2 Current | Analog Status | A |  |  | Y | Y | 60 | 0.1 |  | Calculation | 15321 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
324 | pmp2asMPwr | MPC_pump | 2 | Motor_power | MPC_pump : 2 : Motor_power |  |  | MPC Pump 2 Power | Analog Status | kW |  |  | Y | Y | 60 | 0.1 |  | Calculation | 15322 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
325
326 | pmp2asStartsTdy | MPC_pump | 2 | Number_of_starts | MPC_pump : 2 : Number_of_starts |  |  | MPC Pump 2 Starts Today | Analog Status |  |  |  | Y | Y |  |  |  | Calculation | 10325 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
327 | pmp2asStartsYdy | MPC_pump | 2 | Number_of_starts_yesterday | MPC_pump : 2 : Number_of_starts_yesterday |  |  | MPC Pump 2 Starts Yesterday | Analog Status |  |  |  | Y | Y |  |  |  | Calculation | 10326 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
328 | pmp2asRunHrsTdy | MPC_pump | 2 | Hours_run | MPC_pump : 2 : Hours_run |  |  | MPC Pump 2 Run Hours | Analog Status | Hours |  |  | Y | Y |  |  |  | Calculation | 15325 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0.25 | Absolute | 15 | 0
329 | pmp2asRunHrsYdy | MPC_pump | 2 | Hours_run_yesterday | MPC_pump : 2 : Hours_run_yesterday |  |  | MPC Pump 2 Run Hours Yesterday | Analog Status | Hours |  |  | Y | Y |  |  |  | Calculation | 15326 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
330 | pmp3dsAvailable | MPC_pump | 3 | Available | MPC_pump : 3 : Available | Fault | Ok | MPC Pump 3 Available Alarm | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10346 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
331 | pmp3dsRunning | MPC_pump | 3 | Running | MPC_pump : 3 : Running | Stopped | Running | MPC Pump 3 Running | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10345 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
332 | pmp3dsPresent | MPC_pump | 3 | Present | MPC_pump : 3 : Present | No | Yes | MPC Pump 3 Present | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10349 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
333 | pmp3dsFltMPC | MPC_pump | 3 | Fault_mpc | MPC_pump : 3 : Fault_mpc | Ok | Fault | MPC Pump 3 Pump Fault (MPC) | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10352 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
334 | pmp3dsCommsFlt | MPC_pump | 3 | Comms_fail | MPC_pump : 3 : Comms_fail | Ok | Fault | MPC Pump 3 Comms Fault | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10350 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
335 | pmp3dsAutoActive | MPC_pump | 3 | Auto | MPC_pump : 3 : Auto | No | Yes | MPC Pump 3 Auto Mode | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10348 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
336 | pmp3dsRemModeActive | MPC_pump | 3 | Local_remote | MPC_pump : 3 : Local_remote | No | Yes | MPC Pump 3 Access Mode | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10347 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
337 | pmp3dsFltPmp | MPC_pump | 3 | Fault_pump | MPC_pump : 3 : Fault_pump | Ok | Fault | MPC Pump 3 Pump Fault (Pump) | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10351 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
337.1 | pmp3dsVFDHealthy | MPC_pump | 3 | VFD_healthy | MPC_pump : 3 : VFD_healthy | Fault | Healthy | MPC Pump 3 VFD Healthy Hardwired Status | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10353 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
338 | pmp3asAlarmCode | MPC_pump | 3 | Alarm_code | MPC_pump : 3 : Alarm_code |  |  | MPC Pump 3 Pump Alarm Code | Analog Status |  |  |  | Y | Y |  |  |  | Analog Status | 10344 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
339 | pmp3asSpdPc | MPC_pump | 3 | Speed_Fbk | MPC_pump : 3 : Speed_Fbk |  |  | MPC Pump 3 Speed | Analog Status | % |  |  | Y | Y | 60 | 1 |  | Calculation | 15343 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
340 | pmp3asMCurr | MPC_pump | 3 | Motor_current | MPC_pump : 3 : Motor_current |  |  | MPC Pump 3 Current | Analog Status | A |  |  | Y | Y | 60 | 0.1 |  | Calculation | 15341 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
341 | pmp3asMPwr | MPC_pump | 3 | Motor_power | MPC_pump : 3 : Motor_power |  |  | MPC Pump 3 Power | Analog Status | kW |  |  | Y | Y | 60 | 0.1 |  | Calculation | 15342 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
342
343 | pmp3asStartsTdy | MPC_pump | 3 | Number_of_starts | MPC_pump : 3 : Number_of_starts |  |  | MPC Pump 3 Starts Today | Analog Status |  |  |  | Y | Y |  |  |  | Calculation | 10345 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
344 | pmp3asStartsYdy | MPC_pump | 3 | Number_of_starts_yesterday | MPC_pump : 3 : Number_of_starts_yesterday |  |  | MPC Pump 3 Starts Yesterday | Analog Status |  |  |  | Y | Y |  |  |  | Calculation | 10346 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
345 | pmp3asRunHrsTdy | MPC_pump | 3 | Hours_run | MPC_pump : 3 : Hours_run |  |  | MPC Pump 3 Run Hours | Analog Status | Hours |  |  | Y | Y |  |  |  | Calculation | 15345 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0.25 | Absolute | 15 | 0
346 | pmp3asRunHrsYdy | MPC_pump | 3 | Hours_run_yesterday | MPC_pump : 3 : Hours_run_yesterday |  |  | MPC Pump 3 Run Hours Yesterday | Analog Status | Hours |  |  | Y | Y |  |  |  | Calculation | 15346 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
347 | pmp4dsAvailable | MPC_pump | 4 | Available | MPC_pump : 4 : Available | Fault | Ok | MPC Pump 4 Available Alarm | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10366 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
348 | pmp4dsRunning | MPC_pump | 4 | Running | MPC_pump : 4 : Running | Stopped | Running | MPC Pump 4 Running | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10365 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
349 | pmp4dsPresent | MPC_pump | 4 | Present | MPC_pump : 4 : Present | No | Yes | MPC Pump 4 Present | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10369 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
350 | pmp4dsFltMPC | MPC_pump | 4 | Fault_mpc | MPC_pump : 4 : Fault_mpc | Ok | Fault | MPC Pump 4 Pump Fault (MPC) | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10372 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
351 | pmp4dsCommsFlt | MPC_pump | 4 | Comms_fail | MPC_pump : 4 : Comms_fail | Ok | Fault | MPC Pump 4 Comms Fault | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10370 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
352 | pmp4dsAutoActive | MPC_pump | 4 | Auto | MPC_pump : 4 : Auto | No | Yes | MPC Pump 4 Auto Mode | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10368 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
353 | pmp4dsRemModeActive | MPC_pump | 4 | Local_remote | MPC_pump : 4 : Local_remote | No | Yes | MPC Pump 4 Access Mode | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10367 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
354 | pmp4dsFltPmp | MPC_pump | 4 | Fault_pump | MPC_pump : 4 : Fault_pump | Ok | Fault | MPC Pump 4 Pump Fault (Pump) | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10371 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
354.1 | pmp4dsVFDHealthy | MPC_pump | 4 | VFD_healthy | MPC_pump : 4 : VFD_healthy | Fault | Healthy | MPC Pump 4 VFD Healthy Hardwired Status | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10373 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
355 | pmp4asAlarmCode | MPC_pump | 4 | Alarm_code | MPC_pump : 4 : Alarm_code |  |  | MPC Pump 4 Pump Alarm Code | Analog Status |  |  |  | Y | Y |  |  |  | Analog Status | 10364 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
356 | pmp4asSpdPc | MPC_pump | 4 | Speed_Fbk | MPC_pump : 4 : Speed_Fbk |  |  | MPC Pump 4 Speed | Analog Status | % |  |  | Y | Y | 60 | 1 |  | Calculation | 15363 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
357 | pmp4asMCurr | MPC_pump | 4 | Motor_current | MPC_pump : 4 : Motor_current |  |  | MPC Pump 4 Current | Analog Status | A |  |  | Y | Y | 60 | 0.1 |  | Calculation | 15361 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
358 | pmp4asMPwr | MPC_pump | 4 | Motor_power | MPC_pump : 4 : Motor_power |  |  | MPC Pump 4 Power | Analog Status | kW |  |  | Y | Y | 60 | 0.1 |  | Calculation | 15362 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
359
360 | pmp4asStartsTdy | MPC_pump | 4 | Number_of_starts | MPC_pump : 4 : Number_of_starts |  |  | MPC Pump 4 Starts Today | Analog Status |  |  |  | Y | Y |  |  |  | Calculation | 10365 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
361 | pmp4asStartsYdy | MPC_pump | 4 | Number_of_starts_yesterday | MPC_pump : 4 : Number_of_starts_yesterday |  |  | MPC Pump 4 Starts Yesterday | Analog Status |  |  |  | Y | Y |  |  |  | Calculation | 10366 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
362 | pmp4asRunHrsTdy | MPC_pump | 4 | Hours_run | MPC_pump : 4 : Hours_run |  |  | MPC Pump 4 Run Hours | Analog Status | Hours |  |  | Y | Y |  |  |  | Calculation | 15365 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0.25 | Absolute | 15 | 0
363 | pmp4asRunHrsYdy | MPC_pump | 4 | Hours_run_yesterday | MPC_pump : 4 : Hours_run_yesterday |  |  | MPC Pump 4 Run Hours Yesterday | Analog Status | Hours |  |  | Y | Y |  |  |  | Calculation | 15366 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
364 | pmp5dsAvailable | MPC_pump | 5 | Available | MPC_pump : 5 : Available | Fault | Ok | MPC Pump 5 Available Alarm | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10386 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
365 | pmp5dsRunning | MPC_pump | 5 | Running | MPC_pump : 5 : Running | Stopped | Running | MPC Pump 5 Running | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10385 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
366 | pmp5dsPresent | MPC_pump | 5 | Present | MPC_pump : 5 : Present | No | Yes | MPC Pump 5 Present | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10389 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
367 | pmp5dsFltMPC | MPC_pump | 5 | Fault_mpc | MPC_pump : 5 : Fault_mpc | Ok | Fault | MPC Pump 5 Pump Fault (MPC) | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10392 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
368 | pmp5dsCommsFlt | MPC_pump | 5 | Comms_fail | MPC_pump : 5 : Comms_fail | Ok | Fault | MPC Pump 5 Comms Fault | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10390 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
369 | pmp5dsAutoActive | MPC_pump | 5 | Auto | MPC_pump : 5 : Auto | No | Yes | MPC Pump 5 Auto Mode | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10388 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
370 | pmp5dsRemModeActive | MPC_pump | 5 | Local_remote | MPC_pump : 5 : Local_remote | No | Yes | MPC Pump 5 Access Mode | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10387 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
371 | pmp5dsFltPmp | MPC_pump | 5 | Fault_pump | MPC_pump : 5 : Fault_pump | Ok | Fault | MPC Pump 5 Pump Fault (Pump) | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10391 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
371.1 | pmp5dsVFDHealthy | MPC_pump | 5 | VFD_healthy | MPC_pump : 5 : VFD_healthy | Fault | Healthy | MPC Pump 5 VFD Healthy Hardwired Status | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10393 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
372 | pmp5asAlarmCode | MPC_pump | 5 | Alarm_code | MPC_pump : 5 : Alarm_code |  |  | MPC Pump 5 Pump Alarm Code | Analog Status |  |  |  | Y | Y |  |  |  | Analog Status | 10384 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
373 | pmp5asSpdPc | MPC_pump | 5 | Speed_Fbk | MPC_pump : 5 : Speed_Fbk |  |  | MPC Pump 5 Speed | Analog Status | % |  |  | Y | Y | 60 | 1 |  | Calculation | 15383 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
374 | pmp5asMCurr | MPC_pump | 5 | Motor_current | MPC_pump : 5 : Motor_current |  |  | MPC Pump 5 Current | Analog Status | A |  |  | Y | Y | 60 | 0.1 |  | Calculation | 15381 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
375 | pmp5asMPwr | MPC_pump | 5 | Motor_power | MPC_pump : 5 : Motor_power |  |  | MPC Pump 5 Power | Analog Status | kW |  |  | Y | Y | 60 | 0.1 |  | Calculation | 15382 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
376
377 | pmp5asStartsTdy | MPC_pump | 5 | Number_of_starts | MPC_pump : 5 : Number_of_starts |  |  | MPC Pump 5 Starts Today | Analog Status |  |  |  | Y | Y |  |  |  | Calculation | 10385 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
378 | pmp5asStartsYdy | MPC_pump | 5 | Number_of_starts_yesterday | MPC_pump : 5 : Number_of_starts_yesterday |  |  | MPC Pump 5 Starts Yesterday | Analog Status |  |  |  | Y | Y |  |  |  | Calculation | 10386 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
379 | pmp5asRunHrsTdy | MPC_pump | 5 | Hours_run | MPC_pump : 5 : Hours_run |  |  | MPC Pump 5 Run Hours | Analog Status | Hours |  |  | Y | Y |  |  |  | Calculation | 15385 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0.25 | Absolute | 15 | 0
380 | pmp5asRunHrsYdy | MPC_pump | 5 | Hours_run_yesterday | MPC_pump : 5 : Hours_run_yesterday |  |  | MPC Pump 5 Run Hours Yesterday | Analog Status | Hours |  |  | Y | Y |  |  |  | Calculation | 15386 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
381 | gen1dsATSAutoFlt | Generator | 1 | ATS_not_in_auto | Generator : 1 : ATS_not_in_auto | Ok | Fault | Generator and ATS Not in Auto | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10459 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
382 | gen1dsGenCBTripd | Generator | 1 | CB_tripped | Generator : 1 : CB_tripped | Ok | Fault | Generator CBs Tripped | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10458 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
383 | gen1dsGenFaultAl | Generator | 1 | Common_fault | Generator : 1 : Common_fault | Ok | Fault | Generator Fault | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10455 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
384 | gen1dsGenDoorOpn | Generator | 1 | Door_status | Generator : 1 : Door_status | Closed | Open | Generator Canopy Open | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10457 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
385 | gen1dsGenFuelLow | Generator | 1 | Low_fuel | Generator : 1 : Low_fuel | Ok | Fault | Generator Low Fuel | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10456 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
386 | gen1dsGenFuelMid | Generator | 1 | Mid_fuel | Generator : 1 : Mid_fuel | Ok | Fault | Generator Mid Fuel | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10467 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
387 | gen1dsGenOffSite | Generator | 1 | Offsite | Generator : 1 : Offsite | No | Yes | Generator Off Site | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10454 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
388 | gen1dsGenOnline | Generator | 1 | Online | Generator : 1 : Online | No | Yes | Generator Online | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10452 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
389 | gen1dsGenRunning | Generator | 1 | Running | Generator : 1 : Running | Stopped | Running | Generator Running | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10451 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
390 | gen1dsGenWarning | Generator | 1 | Warning | Generator : 1 : Warning | Ok | Fault | Generator Warning | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10466 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
391 | stn1prInvHysPc | Site | 1 | Invalid_hysteresis_percent | Site : 1 : Invalid_hysteresis_percent |  |  | Site Invalid Hysteresis Percentage | Analog Status | % | [6 empty] | Y | Parameter Feedback | 15000 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
392 | stn1prInvAlmOnDly | Site | 1 | Invalid_on_delay | Site : 1 : Invalid_on_delay |  |  | Site Invalid Alarm On Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10211 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
393 | stn1prInvAlmOffDly | Site | 1 | Invalid_off_delay | Site : 1 : Invalid_off_delay |  |  | Site Invalid Alarm Off Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10210 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
394 | stn1prAlmHysPc | Site | 1 | Alarm_hysteresis_percent | Site : 1 : Alarm_hysteresis_percent |  |  | Site Alarm Hysteresis Percentage | Analog Status | % | [6 empty] | Y | Parameter Feedback | 15001 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
395 | stn1prPreAlmInhDly | Water_pumping_station | 1 | Pressure_alarm_inhibit_delay_Fbk | Water_pumping_station : 1 : Pressure_alarm_inhibit_delay_Fbk |  |  | Pressure Alarm Inhibit Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10213 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
396 | pre1asM | Pressure_gauge | 1 | Pressure_m | Pressure_gauge : 1 : Pressure_m |  |  | Suction Pressure | Analog Status | m |  |  | Y | Y | 60 | 1 |  | Calculation | 15219 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
397 | pre1asMAHD | Pressure_gauge | 1 | Pressure_mahd | Pressure_gauge : 1 : Pressure_mahd |  |  | Suction Pressure mAHD | Analog Status | mAHD |  |  | Y | Y | 15 | 1 |  | Calculation | 15218 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
398 | Pre1prElevation | Pressure_gauge | 1 | Elevation_Rtu | Pressure_gauge : 1 : Elevation_Rtu |  |  | Suction Pressure Elevation | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15220 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
399 | Pre1prEngRange | Pressure_gauge | 1 | Pressure_range_Fbk | Pressure_gauge : 1 : Pressure_range_Fbk |  |  | Suction Pressure Range | Analog Status | m | [6 empty] | Y | Parameter Feedback | 15221 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
400 | Pre1prHiAlmOnDly | Pressure_gauge | 1 | High_limit_on_delay | Pressure_gauge : 1 : High_limit_on_delay |  |  | Suction Pressure High Alarm On Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10223 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
401 | Pre1prHiAlmOffDly | Pressure_gauge | 1 | High_limit_off_delay | Pressure_gauge : 1 : High_limit_off_delay |  |  | Suction Pressure High Alarm Off Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10222 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
402 | Pre1prLoAlmOnDly | Pressure_gauge | 1 | Low_limit_on_delay | Pressure_gauge : 1 : Low_limit_on_delay |  |  | Suction Pressure Low Alarm On Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10225 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
403 | Pre1prLoAlmOffDly | Pressure_gauge | 1 | Low_limit_off_delay | Pressure_gauge : 1 : Low_limit_off_delay |  |  | Suction Pressure Low Alarm Off Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10224 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
403.1 | pre1prLoLoAlmOnDly | Pressure_gauge | 1 | Low_low_limit_on_delay | Pressure_gauge : 1 : Low_low_limit_on_delay |  |  | Suction Pressure Low Low Alarm On Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10247 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
403.2 | pre1prLoLoAlmOffDly | Pressure_gauge | 1 | Low_low_limit_off_delay | Pressure_gauge : 1 : Low_low_limit_off_delay |  |  | Suction Pressure Low Low Alarm Off Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10248 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
404 | pre1acHiAlmLim | Pressure_gauge | 1 | High_limit | Pressure_gauge : 1 : High_limit |  |  | Suction Pressure High Alarm Setpoint | Analog Control | mAHD | [7 empty] | Setpoint | 15556 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
405 | pre1acLoAlmLim | Pressure_gauge | 1 | Low_limit | Pressure_gauge : 1 : Low_limit |  |  | Suction Pressure Low Alarm Setpoint | Analog Control | mAHD | [7 empty] | Setpoint | 15557 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
405.1 | pre1acLoLoAlmLim | Pressure_gauge | 1 | Low_low_limit | Pressure_gauge : 1 : Low_low_limit |  |  | Suction Pressure Low Low Alarm Setpoint | Analog Control | mAHD | [7 empty] | Setpoint | 15558 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
406 | pre1asHiAlmLimFbk | Pressure_gauge | 1 | High_limit_Fbk | Pressure_gauge : 1 : High_limit_Fbk |  |  | Suction Pressure High Alarm Setpoint Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15223 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
407 | pre1asLoAlmLimFbk | Pressure_gauge | 1 | Low_limit_Fbk | Pressure_gauge : 1 : Low_limit_Fbk |  |  | Suction Pressure Low Alarm Setpoint Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15227 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
407.1 | pre1asLoLoAlmLimFbk | Pressure_gauge | 1 | Low_low_limit_Fbk | Pressure_gauge : 1 : Low_low_limit_Fbk |  |  | Suction Pressure Low Low Alarm Setpoint Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15231 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
408 | pre1dsHiAlm | Pressure_gauge | 1 | High | Pressure_gauge : 1 : High | Ok | Fault | Suction Pressure High Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10205 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
409 | pre1dsLoAlm | Pressure_gauge | 1 | Low | Pressure_gauge : 1 : Low | Ok | Fault | Suction Pressure Low Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10206 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
409.1 | pre1dsLoLoAlm | Pressure_gauge | 1 | Low_low | Pressure_gauge : 1 : Low_low | Ok | Fault | Suction Pressure Low Low Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10208 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
410 | pre1dsInvalid | Pressure_gauge | 1 | Invalid | Pressure_gauge : 1 : Invalid | Ok | Fault | Suction Pressure Invalid Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10207 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
411
412
413
414
415 | Pre2prHiAlmOnDly | Pressure_gauge | 2 | High_limit_on_delay | Pressure_gauge : 2 : High_limit_on_delay |  |  | Delivery Pressure High Alarm On Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10228 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
416 | Pre2prHiAlmOffDly | Pressure_gauge | 2 | High_limit_off_delay | Pressure_gauge : 2 : High_limit_off_delay |  |  | Delivery Pressure High Alarm Off Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10227 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
417 | Pre2prLoAlmOnDly | Pressure_gauge | 2 | Low_limit_on_delay | Pressure_gauge : 2 : Low_limit_on_delay |  |  | Delivery Pressure Low Alarm On Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10230 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
418 | Pre2prLoAlmOffDly | Pressure_gauge | 2 | Low_limit_off_delay | Pressure_gauge : 2 : Low_limit_off_delay |  |  | Delivery Pressure Low Alarm Off Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10229 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
419 | pre2acHiAlmLim | Pressure_gauge | 2 | High_limit | Pressure_gauge : 2 : High_limit |  |  | Delivery Pressure High Alarm Setpoint | Analog Control | mAHD | [7 empty] | Setpoint | 15561 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
420 | pre2acLoAlmLim | Pressure_gauge | 2 | Low_limit | Pressure_gauge : 2 : Low_limit |  |  | Delivery Pressure Low Alarm Setpoint | Analog Control | mAHD | [7 empty] | Setpoint | 15562 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
421 | pre2asHiAlmLimFbk | Pressure_gauge | 2 | High_limit_Fbk | Pressure_gauge : 2 : High_limit_Fbk |  |  | Delivery Pressure High Alarm Setpoint Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15239 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
422 | pre2asLoAlmLimFbk | Pressure_gauge | 2 | Low_limit_Fbk | Pressure_gauge : 2 : Low_limit_Fbk |  |  | Delivery Pressure Low Alarm Setpoint Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15243 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
423 | pre2dsHiAlm | Pressure_gauge | 2 | High | Pressure_gauge : 2 : High | Ok | Fault | Active Delivery Pressure High Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10210 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
424 | pre2dsLoAlm | Pressure_gauge | 2 | Low | Pressure_gauge : 2 : Low | Ok | Fault | Active Delivery Pressure Low Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10211 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
425 | pre2dsInvalid | Pressure_gauge | 2 | Invalid | Pressure_gauge : 2 : Invalid | Ok | Fault | Both Delivery Pressures Invalid Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10212 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
426 | stn1asPreDifferential | Water_pumping_station | 1 | Pressure_differential_m | Water_pumping_station : 1 : Pressure_differential_m |  |  | Differential Pressure | Analog Status | m |  |  | Y | Y | 60 | 1 |  | Calculation | 15042 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
427 | Pre1prHiAlmLimDef | Pressure_gauge | 1 | High_limit_default | Pressure_gauge : 1 : High_limit_default |  |  | Suction Pressure High Alarm Setpoint Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15222 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
428 | Pre1prHiAlmLimMax | Pressure_gauge | 1 | High_limit_max | Pressure_gauge : 1 : High_limit_max |  |  | Suction Pressure High Alarm Setpoint Max | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15224 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
429 | Pre1prHiAlmLimMin | Pressure_gauge | 1 | High_limit_min | Pressure_gauge : 1 : High_limit_min |  |  | Suction Pressure High Alarm Setpoint Min | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15225 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
430 | Pre1prLoAlmLimDef | Pressure_gauge | 1 | Low_limit_default | Pressure_gauge : 1 : Low_limit_default |  |  | Suction Pressure Low Alarm Setpoint Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15226 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
431 | Pre1prLoAlmLimMax | Pressure_gauge | 1 | Low_limit_max | Pressure_gauge : 1 : Low_limit_max |  |  | Suction Pressure Low Alarm Setpoint Max | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15228 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
432 | Pre1prLoAlmLimMin | Pressure_gauge | 1 | Low_limit_min | Pressure_gauge : 1 : Low_limit_min |  |  | Suction Pressure Low Alarm Setpoint Min | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15229 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
432.1 | pre1prLoLoAlmLimDef | Pressure_gauge | 1 | Low_low_limit_default | Pressure_gauge : 1 : Low_low_limit_default |  |  | Suction Pressure Low Low Alarm Setpoint Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15230 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
432.2 | pre1prLoLoAlmLimMax | Pressure_gauge | 1 | Low_low_limit_max | Pressure_gauge : 1 : Low_low_limit_max |  |  | Suction Pressure Low Low Alarm Setpoint Max | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15232 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
432.3 | pre1prLoLoAlmLimMin | Pressure_gauge | 1 | Low_low_limit_min | Pressure_gauge : 1 : Low_low_limit_min |  |  | Suction Pressure Low Low Alarm Setpoint Min | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15233 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
433 | Pre2prHiAlmLimDef | Pressure_gauge | 2 | High_limit_default | Pressure_gauge : 2 : High_limit_default |  |  | Delivery Pressure High Alarm Setpoint Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15238 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
434 | Pre2prHiAlmLimMax | Pressure_gauge | 2 | High_limit_max | Pressure_gauge : 2 : High_limit_max |  |  | Delivery Pressure High Alarm Setpoint Max | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15240 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
435 | Pre2prHiAlmLimMin | Pressure_gauge | 2 | High_limit_min | Pressure_gauge : 2 : High_limit_min |  |  | Delivery Pressure High Alarm Setpoint Min | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15241 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
436 | Pre2prLoAlmLimDef | Pressure_gauge | 2 | Low_limit_default | Pressure_gauge : 2 : Low_limit_default |  |  | Delivery Pressure Low Alarm Setpoint Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15242 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
437 | Pre2prLoAlmLimMax | Pressure_gauge | 2 | Low_limit_max | Pressure_gauge : 2 : Low_limit_max |  |  | Delivery Pressure Low Alarm Setpoint Max | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15244 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
438 | Pre2prLoAlmLimMin | Pressure_gauge | 2 | Low_limit_min | Pressure_gauge : 2 : Low_limit_min |  |  | Delivery Pressure Low Alarm Setpoint Min | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15245 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
439 | Pre3prTimeoutOnDly | Pressure_gauge | 3 | Communication_timeout | Pressure_gauge : 3 : Communication_timeout |  |  | Peer Communications Timeout Delay | Analog Status | Minutes | [6 empty] | Y | Parameter Feedback | 10236 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
440 | Pre3prHiAlmOnDly | Pressure_gauge | 3 | High_limit_on_delay | Pressure_gauge : 3 : High_limit_on_delay |  |  | Peer Pressure High Alarm On Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10233 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
441 | Pre3prHiAlmOffDly | Pressure_gauge | 3 | High_limit_off_delay | Pressure_gauge : 3 : High_limit_off_delay |  |  | Peer Pressure High Alarm Off Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10232 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
442 | Pre3prLoAlmOnDly | Pressure_gauge | 3 | Low_limit_on_delay | Pressure_gauge : 3 : Low_limit_on_delay |  |  | Peer Pressure Low Alarm On Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10235 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
443 | Pre3prLoAlmOffDly | Pressure_gauge | 3 | Low_limit_off_delay | Pressure_gauge : 3 : Low_limit_off_delay |  |  | Peer Pressure Low Alarm Off Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10234 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
444 | pre3asMAHD | Pressure_gauge | 3 | Pressure_mahd | Pressure_gauge : 3 : Pressure_mahd |  |  | Peer Pressure mAHD | Analog Status | mAHD |  |  | Y | Y | 15 | 1 |  | Calculation | 15250 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
445 | pre3acHiAlmLim | Pressure_gauge | 3 | High_limit | Pressure_gauge : 3 : High_limit |  |  | Peer Pressure High Alarm Setpoint | Analog Control | mAHD | [7 empty] | Setpoint | 15566 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
446 | pre3acLoAlmLim | Pressure_gauge | 3 | Low_limit | Pressure_gauge : 3 : Low_limit |  |  | Peer Pressure Low Alarm Setpoint | Analog Control | mAHD | [7 empty] | Setpoint | 15567 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
447 | pre3asHiAlmLimFbk | Pressure_gauge | 3 | High_limit_Fbk | Pressure_gauge : 3 : High_limit_Fbk |  |  | Peer Pressure High Alarm Setpoint Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15255 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
448 | pre3asLoAlmLimFbk | Pressure_gauge | 3 | Low_limit_Fbk | Pressure_gauge : 3 : Low_limit_Fbk |  |  | Peer Pressure Low Alarm Setpoint Feedback | Analog Status | mAHD |  |  | Y | Y |  |  |  | Setpoint Feedback | 15259 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
449 | pre3dsHiAlm | Pressure_gauge | 3 | High | Pressure_gauge : 3 : High | Ok | Fault | Peer Pressure High Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10215 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
450 | pre3dsLoAlm | Pressure_gauge | 3 | Low | Pressure_gauge : 3 : Low | Ok | Fault | Peer Pressure Low Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10216 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
451 | pre3dsInvalid | Pressure_gauge | 3 | Invalid | Pressure_gauge : 3 : Invalid | Ok | Fault | Peer Pressure Invalid Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10217 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
452 | pre3dsTimeoutAlm | Pressure_gauge | 3 | Communication_failed | Pressure_gauge : 3 : Communication_failed | Ok | Fault | Peer Communications Timeout Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10218 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
453 | Pre3prHiAlmLimDef | Pressure_gauge | 3 | High_limit_default | Pressure_gauge : 3 : High_limit_default |  |  | Peer Pressure High Alarm Setpoint Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15254 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
454 | Pre3prHiAlmLimMax | Pressure_gauge | 3 | High_limit_max | Pressure_gauge : 3 : High_limit_max |  |  | Peer Pressure High Alarm Setpoint Max | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15256 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
455 | Pre3prHiAlmLimMin | Pressure_gauge | 3 | High_limit_min | Pressure_gauge : 3 : High_limit_min |  |  | Peer Pressure High Alarm Setpoint Min | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15257 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
456 | Pre3prLoAlmLimDef | Pressure_gauge | 3 | Low_limit_default | Pressure_gauge : 3 : Low_limit_default |  |  | Peer Pressure Low Alarm Setpoint Default | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15258 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
457 | Pre3prLoAlmLimMax | Pressure_gauge | 3 | Low_limit_max | Pressure_gauge : 3 : Low_limit_max |  |  | Peer Pressure Low Alarm Setpoint Max | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15260 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
458 | Pre3prLoAlmLimMin | Pressure_gauge | 3 | Low_limit_min | Pressure_gauge : 3 : Low_limit_min |  |  | Peer Pressure Low Alarm Setpoint Min | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | 15261 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
459 | flw1prAlmInhDly | Flow_meter | 1 | Alarm_inhibit_delay | Flow_meter : 1 : Alarm_inhibit_delay |  |  | Delivery Flow Alarm Inhibit Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10220 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
460 | flw1prEngRange | Flow_meter | 1 | Flow_rate_Range_Fbk | Flow_meter : 1 : Flow_rate_Range_Fbk |  |  | Delivery Flow Range | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15203 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
461 | flw1prHiAlmOnDly | Flow_meter | 1 | High_limit_on_delay | Flow_meter : 1 : High_limit_on_delay |  |  | Delivery Flow High Alarm On Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10217 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
462 | flw1prHiAlmOffDly | Flow_meter | 1 | High_limit_off_delay | Flow_meter : 1 : High_limit_off_delay |  |  | Delivery Flow High Alarm Off Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10216 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
463 | flw1prLoAlmOnDly | Flow_meter | 1 | Low_limit_on_delay | Flow_meter : 1 : Low_limit_on_delay |  |  | Delivery Flow Low Alarm On Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10219 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
464 | flw1prLoAlmOffDly | Flow_meter | 1 | Low_limit_off_delay | Flow_meter : 1 : Low_limit_off_delay |  |  | Delivery Flow Low Alarm Off Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10218 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
465 | flw1asLs | Flow_meter | 1 | Flow_rate | Flow_meter : 1 : Flow_rate |  |  | Delivery Flow | Analog Status | L/s |  |  | Y | Y | 15 | 1 |  | Calculation | 15200 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
466 | flw1asKlDay | Flow_meter | 1 | Flow_kl | Flow_meter : 1 : Flow_kl |  |  | Delivery Flow kL/day | Analog Status | kL/day |  |  | Y | Y | 60 | 86.4 |  | Calculation | 15201 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
467 | flw1asVolTdy | Flow_meter | 1 | Volume | Flow_meter : 1 : Volume |  |  | Delivery Flow Volume | Analog Status | kL |  |  | Y | Y |  |  |  | Calculation | 15214 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 1 | Absolute | 15 | 0
468 | flw1asVolYdy | Flow_meter | 1 | Volume_yesterday | Flow_meter : 1 : Volume_yesterday |  |  | Delivery Flow Volume Yesterday | Analog Status | kL |  |  | Y | Y |  |  |  | Calculation | 15215 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
469 | flw1acHiAlmLim | Flow_meter | 1 | High_limit | Flow_meter : 1 : High_limit |  |  | Delivery Flow High Alarm Setpoint | Analog Control | L/s | [7 empty] | Setpoint | 15551 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
470 | flw1acLoAlmLim | Flow_meter | 1 | Low_limit | Flow_meter : 1 : Low_limit |  |  | Delivery Flow Low Alarm Setpoint | Analog Control | L/s | [7 empty] | Setpoint | 15552 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
471 | flw1asHiAlmLimFbk | Flow_meter | 1 | High_limit_Fbk | Flow_meter : 1 : High_limit_Fbk |  |  | Delivery Flow High Alarm Setpoint Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15206 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
472 | flw1asLoAlmLimfbk | Flow_meter | 1 | Low_limit_Fbk | Flow_meter : 1 : Low_limit_Fbk |  |  | Delivery Flow Low Alarm Setpoint Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15210 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
473 | flw1dsInvalid | Flow_meter | 1 | Invalid | Flow_meter : 1 : Invalid | Ok | Fault | Delivery Flow Invalid | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10202 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
474 | flw1dsLoAlm | Flow_meter | 1 | Low | Flow_meter : 1 : Low | Ok | Fault | Delivery Flow Low Alarm | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10201 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
475 | flw1dsHiAlm | Flow_meter | 1 | High | Flow_meter : 1 : High | Ok | Fault | Delivery Flow High Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10200 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
476 | flw1dsVolInv | Flow_meter | 1 | Volume_invalid | Flow_meter : 1 : Volume_invalid | Ok | Fault | Delivery Flow Volume Invalid | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10203 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
477 | flw1prHiAlmLimDef | Flow_meter | 1 | High_limit_default | Flow_meter : 1 : High_limit_default |  |  | Delivery Flow High Alarm Setpoint Default | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15205 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
478 | flw1prHiAlmLimMax | Flow_meter | 1 | High_limit_max | Flow_meter : 1 : High_limit_max |  |  | Delivery Flow High Alarm Setpoint Max | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15207 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
479 | flw1prHiAlmLimMin | Flow_meter | 1 | High_limit_min | Flow_meter : 1 : High_limit_min |  |  | Delivery Flow High Alarm Setpoint Min | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15208 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
480 | flw1prLoAlmLimDef | Flow_meter | 1 | Low_limit_default | Flow_meter : 1 : Low_limit_default |  |  | Delivery Flow Low Alarm Setpoint Default | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15209 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
481 | flw1prLoAlmLimMax | Flow_meter | 1 | Low_limit_max | Flow_meter : 1 : Low_limit_max |  |  | Delivery Flow Low Alarm Setpoint Max | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15211 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
482 | flw1prLoAlmLimMin | Flow_meter | 1 | Low_limit_min | Flow_meter : 1 : Low_limit_min |  |  | Delivery Flow Low Alarm Setpoint Min | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15212 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
483 | flw2prEngRange | Flow_meter | 2 | Flow_rate_Range_Fbk | Flow_meter : 2 : Flow_rate_Range_Fbk |  |  | Low Zone/Bypass Flow Range | Analog Status | L/s | [6 empty] | Y | Parameter Feedback | 15267 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
484 | flw2prHiAlmOnDly | Flow_meter | 2 | High_limit_on_delay | Flow_meter : 2 : High_limit_on_delay |  |  | Low Zone/Bypass Flow High Alarm On Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10239 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
485 | flw2prHiAlmOffDly | Flow_meter | 2 | High_limit_off_delay | Flow_meter : 2 : High_limit_off_delay |  |  | Low Zone/Bypass Flow High Alarm Off Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10238 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
486 | flw2prLoAlmOnDly | Flow_meter | 2 | Low_limit_on_delay | Flow_meter : 2 : Low_limit_on_delay |  |  | Low Zone/Bypass Flow Low Alarm On Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10241 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
487 | flw2prLoAlmOffDly | Flow_meter | 2 | Low_limit_off_delay | Flow_meter : 2 : Low_limit_off_delay |  |  | Low Zone/Bypass Flow Low Alarm Off Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10240 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
488 | flw2asLs | Flow_meter | 2 | Flow_rate | Flow_meter : 2 : Flow_rate |  |  | Low Zone/Bypass Flow | Analog Status | L/s |  |  | Y | Y | 15 | 1 |  | Calculation | 15264 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
489 | flw2asKlDay | Flow_meter | 2 | Flow_kl | Flow_meter : 2 : Flow_kl |  |  | Low Zone/Bypass Flow kL/day | Analog Status | kL/day |  |  | Y | Y | 60 | 86.4 |  | Calculation | 15265 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
490 | flw2asVolTdy | Flow_meter | 2 | Volume | Flow_meter : 2 : Volume |  |  | Low Zone/Bypass Flow Volume | Analog Status | kL |  |  | Y | Y |  |  |  | Calculation | 15278 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 1 | Absolute | 15 | 0
491 | flw2asVolYdy | Flow_meter | 2 | Volume_yesterday | Flow_meter : 2 : Volume_yesterday |  |  | Low Zone/Bypass Flow Volume Yesterday | Analog Status | kL |  |  | Y | Y |  |  |  | Calculation | 15279 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
492 | flw2acHiAlmLim | Flow_meter | 2 | High_limit | Flow_meter : 2 : High_limit |  |  | Low Zone/Bypass Flow High Alarm Setpoint | Analog Control | L/s | [7 empty] | Setpoint | 15571 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
493 | flw2acLoAlmLim | Flow_meter | 2 | Low_limit | Flow_meter : 2 : Low_limit |  |  | Low Zone/Bypass Flow Low Alarm Setpoint | Analog Control | L/s | [7 empty] | Setpoint | 15572 | REAL | VarInput | g30v5 Eng Float AI | Class 0 | Static | None | None
494 | flw2asHiAlmLimFbk | Flow_meter | 2 | High_limit_Fbk | Flow_meter : 2 : High_limit_Fbk |  |  | Low Zone/Bypass Flow High Alarm Setpoint Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15270 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
495 | flw2asLoAlmLimFbk | Flow_meter | 2 | Low_limit_Fbk | Flow_meter : 2 : Low_limit_Fbk |  |  | Low Zone/Bypass Flow Low Alarm Setpoint Feedback | Analog Status | L/s |  |  | Y | Y |  |  |  | Setpoint Feedback | 15274 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
496 | flw2dsInvalid | Flow_meter | 2 | Invalid | Flow_meter : 2 : Invalid | Ok | Fault | Low Zone/Bypass Flow Invalid | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10222 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
497 | flw2dsLoAlm | Flow_meter | 2 | Low | Flow_meter : 2 : Low | Ok | Fault | Low Zone/Bypass Flow Low Alarm | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10221 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
498 | flw2dsHiAlm | Flow_meter | 2 | High | Flow_meter : 2 : High | Ok | Fault | Low Zone/Bypass Flow High Alarm | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10220 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
499 | flw2dsVolInv | Flow_meter | 2 | Volume_invalid | Flow_meter : 2 : Volume_invalid | Ok | Fault | Low Zone/Bypass Flow Volume Invalid | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10223 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
500 | flw2prHiAlmLimDef | Flow_meter | 2 | High_limit_default | Flow_meter : 2 : High_limit_default |  |  | Low Zone/Bypass Flow High Alarm Setpoint Default | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15269 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
501 | flw2prHiAlmLimMax | Flow_meter | 2 | High_limit_max | Flow_meter : 2 : High_limit_max |  |  | Low Zone/Bypass Flow High Alarm Setpoint Max | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15271 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
502 | flw2prHiAlmLimMin | Flow_meter | 2 | High_limit_min | Flow_meter : 2 : High_limit_min |  |  | Low Zone/Bypass Flow High Alarm Setpoint Min | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15272 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
503 | flw2prLoAlmLimDef | Flow_meter | 2 | Low_limit_default | Flow_meter : 2 : Low_limit_default |  |  | Low Zone/Bypass Flow Low Alarm Setpoint Default | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15273 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
504 | flw2prLoAlmLimMax | Flow_meter | 2 | Low_limit_max | Flow_meter : 2 : Low_limit_max |  |  | Low Zone/Bypass Flow Low Alarm Setpoint Max | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15275 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
505 | flw2prLoAlmLimMin | Flow_meter | 2 | Low_limit_min | Flow_meter : 2 : Low_limit_min |  |  | Low Zone/Bypass Flow Low Alarm Setpoint Min | Analog Status | l/s | [6 empty] | Y | Parameter Feedback | 15276 | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
506 | gen1asFuelLevelPc | Generator | 1 | Fuel_level | Generator : 1 : Fuel_level |  |  | Generator Fuel Level | Analog Status | % |  |  | Y | Y | 15 | 2 |  | Analog Status | 15450 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
507 | gen1dsFuelInvalid | Generator | 1 | Fuel_level_invalid | Generator : 1 : Fuel_level_invalid | Ok | Fault | Generator Fuel Level Invalid | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10468 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
508 | pit1dsFlooded | MPC | 1 | Pit_flooded_high | MPC : 1 : Pit_flooded_high | Ok | Fault | Pump Box Pit Flooded | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10225 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
509 | pit2dsFlooded | Flow_meter | 1 | Pit_flooded_high | Flow_meter : 1 : Pit_flooded_high | Ok | Fault | Delivery Flow Meter Pit Flooded | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10228 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
510 | pit3dsFlooded | Flow_meter | 2 | Pit_flooded_high | Flow_meter : 2 : Pit_flooded_high | Ok | Fault | Low Zone/Bypass Flow Meter Pit Flooded | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10231 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
511 | pit1dsProbeFlt | MPC | 1 | Pit_flooded_level_probe_fault | MPC : 1 : Pit_flooded_level_probe_fault | Ok | Fault | Pump Box Pit Level Probe Unhealthy | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10226 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
512 | pit2dsProbeFlt | Flow_meter | 1 | Pit_flooded_level_probe_fault | Flow_meter : 1 : Pit_flooded_level_probe_fault | Ok | Fault | Delivery Flow Meter Pit Level Probe Unhealthy | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10229 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
513 | pit3dsProbeFlt | Flow_meter | 2 | Pit_flooded_level_probe_fault | Flow_meter : 2 : Pit_flooded_level_probe_fault | Ok | Fault | Low Zone/Bypass Flow Meter Pit Level Probe Unhealthy | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10232 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
514 | pitXprFloodedAlmOnDly | Site | 1 | Pit_flooded_on_delay | Site : 1 : Pit_flooded_on_delay |  |  | Pit Flooded Alarm On Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10245 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
515 | pitXprFloodedAlmOffDly | Site | 1 | Pit_flooded_off_delay | Site : 1 : Pit_flooded_off_delay |  |  | Pit Flooded Alarm Off Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10244 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
516 | rtu1asDnpAddress | Rtu | 1 | DNP_address | Rtu : 1 : DNP_address |  |  | RTU Address | Analog Status | [7 empty] | Y | Parameter Feedback | 10011 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
517 | rtu1asHeartbeat | Rtu | 1 | Heartbeat | Rtu : 1 : Heartbeat |  |  | RTU Heartbeat | Analog Status |  |  |  | Y |  |  |  |  | Calculation | 10010 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
518 | stn1dsAbnormOpAlm | Rtu | 1 | Abnormal_operation | Rtu : 1 : Abnormal_operation | Ok | Fault | Abnormal Operation Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10001 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
519 | N/A | Rtu | 1 | Heartbeat_failed | Rtu : 1 : Heartbeat_failed | Ok | Fault | Heartbeat Failed Alarm (SCADA Generated) | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | N/A | BOOL | N/A | N/A | N/A | N/A |  |  | 1 | 0
520 | stn1dsInitFltAlm | Rtu | 1 | Initialisation_error | Rtu : 1 : Initialisation_error | Ok | Fault | Initialisation Failed Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10057 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
521 | rtu1dsErrorSysAlm | Rtu | 1 | System_error | Rtu : 1 : System_error | Ok | Fault | RTU System Error | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10000 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
522 | stn1dcAbnormOpAlmRst | Rtu | 1 | Abnormal_operation_reset | Rtu : 1 : Abnormal_operation_reset | Off | Reset | Abnormal Operation Reset | Digital Control |  | Alarm(2) (Control Fail) | [6 empty] | Digital Control | 10500 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
523 | stn1prSuppAuthPwrFlOnDly | Site | 1 | Energex_fail_delay | Site : 1 : Energex_fail_delay |  |  | Energex Power Fail Alarm Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10026 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
524 | stn1prMainsPwrFailOnDly | Water_pumping_station | 1 | Mains_fail_delay | Water_pumping_station : 1 : Mains_fail_delay |  |  | Mains Power Fail Alarm Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10025 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
525 | stn1prSurgeDivFlOnDly | Site | 1 | Surge_diverter_fail_delay | Site : 1 : Surge_diverter_fail_delay |  |  | Surge Diverter and Filter Fault Alarm Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10029 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
526 | rtu1prPwrFailOnDly | Rtu | 1 | Mains_power_fail_delay | Rtu : 1 : Mains_power_fail_delay |  |  | RTU Power Fail Alarm Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10027 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
527 | rtu1prBattFailOnDly | Rtu | 1 | Battery_fail_delay | Rtu : 1 : Battery_fail_delay |  |  | RTU Battery Fail Alarm Delay | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10028 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
528 | stn1dsSuppAuthPwrFl | Site | 1 | Energex_power | Site : 1 : Energex_power | Ok | Fault | Energex Power Fail Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10008 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
529 | stn1dsMainsPwrFail | Water_pumping_station | 1 | Mains_fail | Water_pumping_station : 1 : Mains_fail | Ok | Fault | Mains Power Fail Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10007 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
530 | stn1dsSurgeDivFl | Site | 1 | Surge_diverter_fail | Site : 1 : Surge_diverter_fail | Ok | Fault | Surge Diverter and Filter Fault Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10011 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
531 | rtu1dsPwrFail | Rtu | 1 | Mains_power | Rtu : 1 : Mains_power | Ok | Fault | RTU Power Fail Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10009 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
532 | rtu1dsBattFail | Rtu | 1 | Battery_power | Rtu : 1 : Battery_power | Ok | Fault | RTU Battery Fail Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10010 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
533 | stn1dsEStopFltAlm | Water_pumping_station | 1 | Emergency_stop | Water_pumping_station : 1 : Emergency_stop | Ok | Fault | Emergency Stop | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10060 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
534 | stn1prIntruderAlmOnDly | Security | 1 | Intruder_delay | Security : 1 : Intruder_delay |  |  | Intruder Alarm Delay | Analog Status | min | [6 empty] | Y | Parameter Feedback | 10024 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
535 | stn1dsDoorsOpen | Security | 1 | Door_status | Security : 1 : Door_status | Closed | Open | Door Open | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | 10004 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
536 | stn1dsIntruderAlm | Security | 1 | Intruder | Security : 1 : Intruder | Ok | Fault | Intruder Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10005 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
537 | stn1asWiretoWaterEfficency | Site | 1 | Wire_to_water_efficiency | Site : 1 : Wire_to_water_efficiency |  |  | Wire to Water Efficiency | Analog Status |  |  |  | Y | Y | 60 | 0.01 |  | Analog Status | 15008 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
538 | mpc1prSPMMFltDB | MPC | 1 | Setpoint_mismatch_deadband | MPC : 1 : Setpoint_mismatch_deadband |  |  | MPC Setpoint Mismatch Deadband | Analog Status | Units | [6 empty] | Y | Parameter Feedback | 10406 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
539 | gen1prGenTimingBuffer | Generator | 1 | Generator_timing_buffer | Generator : 1 : Generator_timing_buffer |  |  | Generator Timing Buffer | Analog Status | s | [6 empty] | Y | Parameter Feedback | 10462 | DINT | VarOutput | g30v2 16bit Analog In | Class 0 | Static | None | None | 15 | 0
540 | gen1dcReset | Generator | 1 | Remote_reset | Generator : 1 : Remote_reset | Off | Reset | Generator Reset | Digital Control |  | Alarm(2) (Control Fail) | [6 empty] | Digital Control | 10676 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
541 | rtu1asSystemError | Rtu | 1 | System_error_code | Rtu : 1 : System_error_code |  |  | RTU System Error Register | Analog Status |  |  |  | Y | Y |  |  |  | Analog Status | 10073 | DINT | VarOutput | g30v2 16bit Analog In | Class 3 | Buffered | 0 | Absolute | 15 | 0
542 | rtu1dsOnBoardIOFlt | Rtu | 1 | Onboard_io_fault | Rtu : 1 : Onboard_io_fault | Ok | Fault | RTU On Board IO Fault | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10012 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
543 | rtu1dsExpansionIOFlt | Rtu | 1 | Expansion_io_fault | Rtu : 1 : Expansion_io_fault | Ok | Fault | RTU Expansion IO Fault | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10013 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
544 | stn1dsLFireSelected | Water_pumping_station | 1 | Fire_switch_active | Water_pumping_station : 1 : Fire_switch_active | Control | Fire | Fire Switch Active | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10069 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
545 | stn1asFixSpdSP | Water_pumping_station | 1 | Fixed_speed_mode_current_system_performance | Water_pumping_station : 1 : Fixed_speed_mode_current_system_performance |  |  | Fixed Speed Mode Current Performance Setpoint | Analog Status | % |  |  | Y | Y |  |  |  | Analog Status | 15066 | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | 0 | Absolute | 15 | 0
546 |  | Rtu | 1 | Isagraf_stopped | Rtu : 1 : Isagraf_stopped | Ok | Fault | RTU ISaGRAF not running | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 50100 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
547 | rtu1dsOperateFailed | Rtu | 1 | Operate_fail | Rtu : 1 : Operate_fail | Ok | Fault | General/Aggregate Operate Function Block Failure Status | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10058 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
548 | rtu1dsGenEvtFailed | Rtu | 1 | Generate_event_fail | Rtu : 1 : Generate_event_fail | Ok | Fault | General/Aggregate Generate Event Function Block Failure Status | Digital Status |  | Event | Y | [5 empty] | Digital Status/Alarm | 10059 | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
549 | rtu1dcFltRst | Rtu | 1 | Fault_reset | Rtu : 1 : Fault_reset | Off | Reset | RTU Fault Reset | Digital Control |  | Alarm(2) (Control Fail) | [6 empty] | Digital Control | 10502 | BOOL | VarInput | g1v1 Binary Input | Class 0 | Static
550 | pre2AasM | Pressure_gauge | 2A | Pressure_m | Pressure_gauge : 2A : Pressure_m |  |  | Main Delivery Pressure | Analog Status | m |  |  | Y | Y | 60 | 1 |  | Calculation | TBA | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
551 | pre2AasMAHD | Pressure_gauge | 2A | Pressure_mahd | Pressure_gauge : 2A : Pressure_mahd |  |  | Main Delivery Pressure mAHD | Analog Status | mAHD |  |  | Y | Y | 15 | 1 |  | Calculation | TBA | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
552 | Pre2AprElevation | Pressure_gauge | 2A | Elevation_Rtu | Pressure_gauge : 2A : Elevation_Rtu |  |  | Main Delivery Pressure Elevation | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | TBA | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
553 | Pre2AprEngRange | Pressure_gauge | 2A | Pressure_range_Fbk | Pressure_gauge : 2A : Pressure_range_Fbk |  |  | Main Delivery Pressure Range | Analog Status | m | [6 empty] | Y | Parameter Feedback | TBA | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
554 | pre2AdsHiAlm | Pressure_gauge | 2A | High | Pressure_gauge : 2A : High | Ok | Fault | Main Delivery Pressure High Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | TBA | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
555 | pre2AdsLoAlm | Pressure_gauge | 2A | Low | Pressure_gauge : 2A : Low | Ok | Fault | Main Delivery Pressure Low Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | TBA | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
556 | pre2AdsInvalid | Pressure_gauge | 2A | Invalid | Pressure_gauge : 2A : Invalid | Ok | Fault | Main Delivery Pressure Invalid Alarm | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | TBA | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
557 | pre2BasM | Pressure_gauge | 2B | Pressure_m | Pressure_gauge : 2B : Pressure_m |  |  | Backup Delivery Pressure | Analog Status | m |  |  | Y | Y | 60 | 1 |  | Calculation | TBA | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
558 | pre2BasMAHD | Pressure_gauge | 2B | Pressure_mahd | Pressure_gauge : 2B : Pressure_mahd |  |  | Backup Delivery Pressure mAHD | Analog Status | mAHD |  |  | Y | Y | 15 | 1 |  | Calculation | TBA | REAL | VarOutput | g30v5 Eng Float AI | Class 3 | Buffered | None | None | 15 | 0
559 | pre2BprElevation | Pressure_gauge | 2B | Elevation_Rtu | Pressure_gauge : 2B : Elevation_Rtu |  |  | Backup Delivery Pressure Elevation | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | TBA | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
560 | pre2BprEngRange | Pressure_gauge | 2B | Pressure_range_Fbk | Pressure_gauge : 2B : Pressure_range_Fbk |  |  | Backup Delivery Pressure Range | Analog Status | m | [6 empty] | Y | Parameter Feedback | TBA | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
561 | pre2BdsHiAlm | Pressure_gauge | 2B | High | Pressure_gauge : 2B : High | Ok | Fault | Backup Delivery Pressure High Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | TBA | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
562 | pre2BdsLoAlm | Pressure_gauge | 2B | Low | Pressure_gauge : 2B : Low | Ok | Fault | Backup Delivery Pressure Low Alarm | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | TBA | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
563 | pre2BdsInvalid | Pressure_gauge | 2B | Invalid | Pressure_gauge : 2B : Invalid | Ok | Fault | Backup Delivery Pressure Invalid Alarm | Digital Status |  | Alarm(2) | Y | [5 empty] | Digital Status/Alarm | TBA | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
564 | TBA | TBA | TBA | TBA | TBA | Ok | Fault | Delivery Pressure Sensor Difference Alarm | Digital Status |  | Alarm (2) | Y | [5 empty] | Digital Status/Alarm | TBA | BOOL | VarOutput | g1v1 Binary Input | Class 3 | Buffered |  |  | 1 | 0
565 | TBA | TBA | TBA | TBA | TBA |  |  | Delivery Pressure Sensor Difference Deadband | Analog Status | mAHD | [6 empty] | Y | Parameter Feedback | TBA | REAL | VarOutput | g30v5 Eng Float AI | Class 0 | Static | None | None | 15 | 0
566 | TBA | Water_pumping_station | 1 | Control_stop | Water_pumping_station : 1 : Control_stop | Ok | Fault | Control Stop | Digital Status |  | Alarm(1) | Y | [5 empty] | Digital Status/Alarm | 10060 | BOOL | VarOutput | g1v1 Binary Input | Class 1 | Unsolicited |  |  | 1 | 0
Points Removed from v5.0
Points Added/Modified v 6.x
Note: If only main discharge PG is installed (i.e. Option E3 – Redundant Discharge Pressure Transmitter Fitted = true), then pre2AdsInvalid must be configured as a Priority 1 Alarm.