## Cover
Using this Guideline
This document details the requirements and deliverables for the design, construction and compliance of Non-standard Connection Water Approvals involving water and wastewater complex assets (treatment, storage or pumping facilities). Development customers should use this guideline to scope work, avoid duplication and manage requirements and documentation.
Details | Enter text below
PNT Number: | Enter PNT here
Type of Asset: | Sewer Pump Station
Asset's Address: | Enter ASSET's address here
Submitted by (Consultant): | Enter CONSULTANT's name here
To offer feedback or for more information contact Urban Utilities Developer Services:
Email developmentenquiries@urbanutilities.com.au
Phone 07 3432 2200

## App Tracker
PNT Number: |  | Enter PNT here |  |  | Each time communication occurs between UU and the Consultants, use this tracker to share high level information.
Type of Asset: |  | Sewer Pump Station
Asset's Address: |  | Enter ASSET's address here
Submitted by (Consultant): |  | Enter CONSULTANT's name here
Application tracker
Date | UU or Consultant (select one) | Stage eg D1, C1, COM1 | Reason (select one) | Comment

## How to submit
How to submit complex asset documents
Your development will progress through project milestones from design to compliance acceptance. Submission of your Milestone 1 package is only permitted after the Water Approval Decision Notice has been issued. Lodging your design, construction and compliance documentation packages involves a two-step process: 1. Upload documents/drawings as individual items via the Developer Services Portal. 2. Notify the relevant Urban Utilities contact via email listed at the top of each tab To help with an efficient review of your documents, please ensure that the package you submit at each milestone is consolidated and complete and includes this document. Well organised documents save time during the review and assist your development to progress through the process as quickly as possible.
To find out more about our service standards, including commitments and timeframes, visit: https://urbanutilities.com.au/development/help-and-advice/standards-and-guidelines
To access Urban Utilities’ guidelines, go to: https://www.urbanutilities.com.au/development/help-and-advice/standards-and-guidelines

## Design
Communicating with Urban Utilities during DESIGN
Once the review of your development design begins, an Urban Utilities’ design engineer will be assigned as your main contact for ALL DESIGN Milestones. This person will liaise on your behalf, enterprise wide, on design assessment matters. When uploading documents for this stage to the Developer Services Portal, please also advise the team by email: developmentenquiries@urbanutilities.com.au
Complex Asset Deliverable Tracking Checklist - DESIGN
PNT Number: |  | Enter PNT here |  | Information Requests can be issued for all design milestone submission.
Type of Asset: |  | Sewer Pump Station
Asset's Address: |  | Enter ASSET's address here |  | Design Milestone approval shall be subject to successful addressing of the information request items.
Submitted by (Consultant): |  | Enter CONSULTANT's name here |  | All design submissions shall be certified by relevant RPEQ engineer
Checklist reviewed by (UU): |  | UU Engineer's name goes here
Stage | Item No | Design Tasks | Deliverable's name | Date Consultant sent to UU | Consultant uploaded Deliverable and Appendices | Consultant comment | Appendices (Minimum requirements) | UU received | UU review & comments
D1 - Design Milestone 1 - Basis of Design | 1 | Design Kick off meeting
| 2 | Development of Design Management Plan | Design Management Plan (list all parties and responsbility matrix showing roles and responsbilities, overview of project) |  |  |  | Schedule/program for design of the asset
Meeting Minutes from the Design Kick off meeting
| 3 | Development of the site specific Basis of Design | Basis of Design Basis of Design Report (TEM687 for Sewer Pump Station or TEM688 for Water Booster/Pump Station) |  |  |  | 1.All appendices included with TEM687 or TEM688
2.Approved Planning Reports issued prior to water approval stage
3. Water approval
4.Site Layout Plan
5.Site Access Plan including a swept path diagram for maintenance vehicle access path to the requirement of the Basis of Design
6.List of deviation from the standards with justification for UU endorsement (If any)
7.Minutes from the standards' alignment meeting (if there is any)
| 4 | Meeting to confirm the standard's alignment (optional) | Meeting held
Stage | Item No | Tasks | Deliverable's name | Date Consultant sent to UU | Consultant uploaded Deliverable and Appendices Y/NA | Consultant comment | Appendices (Minimum requirements) | UU received | UU review & comments
D2 - Design Milestone 2 - Preliminary Design | 5 | Responses to all Urban Utilities Review Comments on Milestone 1 Desktop review of the scope and available relevant data, drawings and specifications needed for the Functional Design Preliminary Constructability Review with the development of Preliminary Construction Methodology Hydraulic Analysis Development of the Prelimary Design, functional design and P&ID Complete Engineering Survey investigation including cadastral connection service location and potholing Geotechnical Investigation for SPS area and the rising main alignment Pump Selection as per the requirement of TEM687 or TEM688 Noise assessment Odour Assessment (for SPS) Ecological Assessment Cultural Heritage Assessment | Preliminary Design Report covering Background, Site Tenure Details inlcuding easement reuirement as per UU Easement Guideline, Design Criteria, design Flows, Hydraulics, SPS Design, Pump selection, Control philosophy, Rising Main design, Gravity sewer design, preliminary structural design, Ecological Assessment, Cultural Heritage Assessment, Safety in Design, constructability review, departures from standard if any any other items relevant to the specific site |  |  |  | 1.Preliminary design including locality and outline layout plan for the proposed infrastructure, basic details and elevations, pipework route plans (rising main and pump station internals), preliminary long sections of rising main with inputs from engineering survey.
2.Functional design to demonstrate maintenance requirements including design deliverables suitable for the managing consultant to negotiate with affected stakeholders for construction access, site stormwater design and permanent acquisition of land
3. Emergency Storage Calculations (SPS Site)
4. Buoyancy Calculations (SPS Site)
5.Pump selection deliverables including the pump selection evaluation with NPV Analysis and pump data sheets.
6. Safety in Design Risk register (to be continuously reviewed throughout the project).
7.30% TEM618 Asset Management Equipment Register.
8.Site specific functional specification for electrical, instrumentation and control including process and Instrumentation Diagram.
9. Information from engineering survey with Cadastral connection, service location and potholing.
10. Geotechnical Assessment Report.
11. Noise Assessment Report.
12. Odour Assessment Report (for SPS).
13. Ecological Assessment Report.
14. Cultural Heritage Assessment.
15. Council approval.
16. Any other relevant approval
17. Comments Register with the responses for the comments issued by UU at Design Milestone 1 (shall be updated with subsequent review)
18. Any other site specific relevant items
Stage | Item No | Tasks | Deliverable's name | Date Consultant sent to UU | Consultant uploaded Deliverable and Appendices | Consultant comment | Appendices (Minimum requirements) | UU received | UU review & comments
D3 - Design Milestone 3 - Detail Design | 6 | Responses to all Urban Utilities Review Comments on Milestone 2 review comments Safety in Design Risk Assessment Detailed Hydraulic Analysis including surge Analysis, fatigue analysis where required Development of full set of engineering drawings for Civil, Structural and Mechanical components of SPS/WBS and Rising Main Development of Full set electrical drawings and all other electrical deliverables Detailed Constructability Review with the development of Construction Methodology Carry out radio survey/4G Survey Prepare Environmentally Relevant Activity (ERA) License Application TEM671 (required when PS capacity>40kL/hr) Finalize TEM618 Asset Management Equipment Register | Detailed Design Report with detailed Engineering drawings for all disciplines and other deliverables covering Background, Design Criteria, design Flows, Hydraulics, SPS Design, Pump selection, Control philosophy, Rising Main design, Gravity sewer design, Structural design, Electrical and Control System Design, Ecological Assessment, Cultural Heritage Assessment, Safety in Design, constructability review, departures from standard if any any other items relevant to the specific site |  |  |  | 1.Full set of detailed engineering drawings for Civil, Structural and mechanical for all components (including site stormwater, fencing, retaining walls etc.) of SPS/WBS and the Rising Main
2.Full set of electrical drawings with all electrical and control system deliverables: Radio/4G Survey Reports Power System Analysis Site Specific Functional Specification I/O list Lightning Assessment study Switchboard Ventilation Claculation Rerpot Switchboard Design Verification Report
3.All relevant design calculations and reports for all disciplines (Civil, Mechanical, Structural, Hydraulics, Stormwater, Electrical and Control system. Environmental)
4.Safety in Design Report with Safety in Design Risk Register
5. TEM671
6. TEM618
7.Comments Register with the responses for the comments issued by UU at Design Milestone 1 and 2 ( (shall be updated with subsequent review))
8. Any items that was not submitted previously
9.All deliverables submitted with previous stages shall be included with the Appendix of the design report

## Construct
Communicating with Urban Utilities during CONSTRUCTION, incl Factory Acceptance Testing (FAT) and Site Acceptance Testing (SAT)
Once a Design Approval has been issued, your one point of contact with Urban Utilities will become the Coordinator Developer Projects. This person will, on your behalf, liaise enterprise wide, as required on construction matters. When submitting documents for this stage, please use the following naming protocol for the uploaded file: Stage-Item Number-Construction Task eg. CONS1-Item 4-Construction Program When uploading documents for this stage in the Developer Services Portal, please also advise the team by email: DevelopmentComplexAsset@urbanutilities.com.au In addition, you are requested to submit notices to Urban Utilities, where establishment cost variation may arise in the delivery of conditioned trunk infrastructure. This requirement is specified under the Water Netserv Plan and/or typical Water Infrastructure Agreements (WIAs), whichever applies to your Water Approval. Please advise of this situation by emailing: ICNEnquiries@urbanutilities.com.au and liaison will occur about subsequent steps.
Complex Asset Deliverable Tracking Checklist - CONSTRUCTION
PNT Number: |  |  | Enter PNT here
Type of Asset: |  |  | Sewer Pump Station
Asset's Address: |  |  | Enter ASSET's address here
Submitted by (Consultant): |  |  | Enter CONSULTANT's name here
Checklist reviewed by (UU):
Date Consultant sent to UU | Stage | Item No | Construction Tasks | Consultant uploaded Task | Consultant comment | UU received | UU review & comments
| CONS 1 - Prestart | 1 | Stamped IFC drawings (as per item 17) delivered to all stakeholders at least three (3) business days before the proposed pre-start site meeting.
|  | 2 | Safety management plan
|  | 3 | Construction management plan
|  | 4 | Construction program
|  | 5 | Traffic management plan
|  | 6 | Quality management plan including ITPs and ITP schedule
|  | 7 | Construction and post construction environmental management plan
|  | 8 | Network Assess Permit (NAP) for the new connection of the new asset
|  | 9A | Approved site-specific fundtional specification
|  | 9B | Power System Analysis (PSA)
|  | 9C | Functional specification
|  | 9D | Radio survey 4G Survey
Date Consultant sent to UU | Stage | Item No | Construction Tasks | Consultant uploaded Task | Consultant comment | UU received | UU review & comments
| CONS 2 - FAT/pre-commissioning | 10 | Completed Factory Acceptance Test (FAT) document
|  | 11 | Change management form (FOR603)
|  | 12 | Implementation test plan (control systems especially for additions to SCADA)
|  | 13 | Access authorisation for Instrumentation & Control System (ICS) works (FOR646)
|  | 14 | Approved site-specific functional specification
|  | 15 | Approved electrical drawings (as per IFC)
|  | 16 | Enterprise historian tag list (for new tags)
|  | 17 | Control Systems Risk assessment
|  | 18 | Site acceptance test sheets
|  | 19 | Urban Utilities enterprise historian request for point updates (FOR1076)
|  | 20 | Off line Pre-developed SCADA page
|  | 21 | Electrical schematics point to point green line drawings
|  | 22 | Function check electrical drawings yellow line
|  | 23 | Pre-factory inspections tests signed by Urban Utilities (CHE135)
|  | 24 | Switchboard test pack (switchboard specific requirements)
|  | 25 | Full set of electrical schematics identified as point to point and function tested (e.g. green or orange)
|  | 26 | Pre-factory inspections tests completed and signed by the contractor (CHE135)
|  | 27 | Control systems pre-FAT testing documents
|  | 28 | Contractors mandatory test sheets
|  | 29 | FAT appointment time
|  | 30 | ERA63 Approval from Environmentally Relevant Activity & TEM671 Form
Date Consultant sent to UU | Stage | Item No | Construction Tasks | Consultant uploaded Task | Consultant comment | UU received | UU review & comments
| CONS3 - SAT/ commissioning | 31 | Physical Input/Output (IO) list
|  | 32 | Maintenance schedules TEM655
|  | 33 | Spare parts list TEM654
|  | 34 | Lubrication schedule TEM653
|  | 35 | Vendor manuals
|  | 36 | Operating manual TEM656
|  | 37 | Final Asset Management Equipment Register TEM618 (including commissioning date)
|  | 38 | Completed FAT document
|  | 39 | Change management form (FOR603)
|  | 40 | Implementation test plan
|  | 41 | Access authorisation for ICS works (FOR646)
|  | 42 | Approved site-specific functional specification
|  | 43 | Approved electrical drawings (as per IFC)
|  | 44 | Enterprise historian tag list (for new tags)
|  | 45 | Risk assessment (if required)
|  | 46 | Site acceptance test sheets to be used
|  | 47 | Urban Utilities enterprise historian request for point updates (FOR1076)
|  | 48 | Pre-developed SCADA page
|  | 49 | Pre-factory inspections tests completed/signed by UU (CHE135)
|  | 50 | Switchboard Test Pack – Switchboard Specific Requirements

## FAT-SAT
Complex Asset Deliverable Tracking Checklist - FAT SAT
PNT Number: |  | Enter PNT here
Type of Asset: |  | Sewer Pump Station
Asset's Address: |  | Enter ASSET's address here
Submitted by (Consultant/Contractor):
Checklist reviewed by (UU):
FACTORY ACCEPTANCE TESTING (FAT) & SITE ACCEPTANCE TESTING (SAT)
Milestone | Check | Key Tasks | Receive Date
6 - Prestart |  | Stamped IFC drawings (as per item 17) delivered to all stakeholders at least three (3) business days before the proposed pre-start site meeting.
Safety management plan
Construction management plan
|  | Construction program |  |  | -
Traffic management plan
Quality management plan including ITPs and ITP schedule
Construction environmental management plan
Network Assess Permit (NAP) for the new connection of the new asset
Approved site-s[ecific fundtional specification
Power System Analysis (PSA)
Functional specification
Radio survey
7 - FAT/pre-commissioning |  | Completed Factory Acceptance Test (FAT) document
Change management form (FOR603)
Implementation test plan (control systems especially for additions to SCADA)
Access authorisation for Instrumentation & Control System (ICS) works (FOR646)
Approved site-specific functional specification
Approved electrical drawings (as per IFC)
Enterprise historian tag list (for new tags)
Risk assessment (if required)
Site acceptance test sheets
Urban Utilities enterprise historian request for point updates (FOR1076)
Pre-developed SCADA page
Electrical schematics green line drawings
Function check electrical drawings
Pre-factory inspections tests signed by Urban Utilities (CHE135)
Switchboard test pack (switchboard specific requirements)
Full set of electrical schematics identified as point to point and function tested (e.g. green or orange)
Pre-factory inspections tests completed and signed by the contractor (CHE135)
Control systems pre-FAT testing documents
Contractors mandatory test sheets
FAT appointment time
ERA63 Approval from Environmentally Relevant Activity & TEM671 Form
8 - SAT/commissioning |  | Physical Input/Output (IO) list
Maintenance schedules TEM655
Spare parts list TEM654
Lubrication schedule TEM653
Vendor manuals
Operating manual TEM656
Final Asset Management Equipment Register TEM618 (including commissioning date)
Completed FAT document
Change management form (FOR603)
Implementation test plan
Access authorisation for ICS works (FOR646)
Approved site-specific functional specification
Approved electrical drawings (as per IFC)
Risk assessment (if required)
Site acceptance test sheets to be used
Urban Utilities enterprise historian request for point updates (FOR1076)
Pre-developed SCADA page
Pre-factory inspections tests completed/signed by UU (CHE135)
Switchboard Test Pack – Switchboard Specific Requirements
PRE-FAT | Contractor provided | The electrical contractor carries out a pre-FAT: the suite of documents generated from this FAT are sent to the Principal Contractor (consultant) and then on to UU for review. This is required prior to being able to make an appointment for FAT | UU received date | UU review & comments
A full set of signed and dated marked up electrical schematics that indicate that a point to point test has been done and that a full functionality test has been done, it can be on two separate schematic sets or on the same set two colours
A quality check document completed and signed by the electrical contractor; it is to be similar to UU document CHE135
Contractors test documents for the integrity and quality of the switchboard build including ITC’s, and mandatory tests
The control System Engineer’s point to point (as per the I/O list) and functionality tests ITP completed as tested )Control systems FAT document)
Photos of the Switchboard
If there is 3rd party interface equipment, it must be connected to the switchboard for the Pre-FAT (i.e. externally mounted VFD's and Grundfos pump assemblies)
A design verification report (DVR) and a Compliance Certificate for the construction (FAT and for the installation SAT) is to be provided
FAT | Contractor provided | The contractor carries out the "UU" witnessed FAT. The Control Systems Change Request can now be submitted along with the supporting documents in one submission. Documents listed. The FAT resultant documents are then supporting documents for the control systems change request FOR603 | UU received date | UU review & comments
A reviewed and accepted Site-Specific Functional Specification by the UU network engineer
A copy of the System Engineers FAT test report
A copy of the SAT commissioning plan, and the SCADA ITP. The ITP needs to include verifying that the contractor is using the correct version of SCADA.
A copy of a full set the Electrical Construction Schematics IFC
A copy of the Enterprise Historian new data base tags, preliminary
The FOR603 V12 Change Request application signed correctly by all parties, note this takes 13 days (3 for review, 10 to process).
The Remote Corporate Access application started by the UU via the UU workers portal IT request
Control Systems risk analysis
Approved UU networks shut plan
PRE-SAT | Contractor provided | The electrical contractor and the control systems engineer will do Pre-SAT, site point to point, functionality and establish communications with the Clear SCADA via the telemetry. All mechanical equipment will be bled and pressure tested, pipe work is to be disinfected with a accepted result. The PreSat proceedure and resultant documents are used to proceed to the SAT | UU received date | UU review & comments
An approved Change Request Form (FOR603)
A Remote Control Systems Authorisation (FOR646).
A Network Access Permit
The TEM618 uploaded
A redlined marked up full set of electrical schematics, maintenance schedule, and recommended parts list / lubrication schedule. The full set of pre commissioning documents, Mechanical and civils testing documents, The switchboard pre energisation mandatory and contactors test sheets
TEM 655 Maintenance Schedule
TEM 656 Training Manual
TEM 654 Spares list
SAT- Prerequisites | Contractor's Check | Use the previously submitted control systems commissioning ITP. The SAT is more comprehensive where the system is tested against the Site-Specific Functional specification (SSFS) from the site devices to SCADA for alarms, status, controls and trends. The contractor will monitor the site for performance post commissioning rectify any issues during the proving period (two weeks). During this two week period | UU received date | UU review & comments
Deliver a copy of the HMI project file
Deliver a copy of the progrm files of the VFD.s and other equipment devices
If a Grundfos pu,p assembly has been used a complete back up of the MPC and each VFD program files (one file)
Testing documents: These documents would have mainly been submitted as part of obtaining the control systems change request approval (FOR603)
Required before commissioning: TEM618 TEM653, TEM654, TEM655, TEM656, as per the pre SAT required documents
During the post proving period. Provide a complete set of the Site Acceptance test sheets, a full set of "as built" electrical schematics, PDF and CAD. A register of any defects, TEM618 as installed, all the contractor testing documents, eg Control systems commisioning ITP report, "as built" site specific functional specification (SSFS)
Approved UU networks shut plan
SAT- Post SAT | Contractor's Check |  | UU received date | UU review & comments
Deliver a copy of the Sites RTU code and data base files

## Compliance
Communicating with Urban Utilities during COMPLIANCE
When submitting documents for this stage, please use the following naming protocol for the uploaded file: Stage-Item Number-Compliance Task eg. COMPL1-Item 4A-As constructed ADAC file Once the review of your development's compliance package begins, contact Coordinator Developer Projects for ALL COMPLIANCE matters. When uploading documents for this stage to the Developer Services Portal, please also advise the team by email: DevelopmentComplexAsset@urbanutilities.com.au SPECIAL NOTE: For matters relating to As-Constructed Certification and Maintenance Bond email your request also to: Development.Compliance@urbanutilities.com.au
Complex Asset Deliverable Tracking Checklist COMPLIANCE
|  | PNT Number: |  |  | Enter PNT here
|  | Type of Asset: |  |  | Sewer Pump Station
|  | Asset's Address: |  |  | Enter ASSET's address here
Submitted by (Consultant):
Checklist reviewed by (UU):
Stage | Date Consultant sent to UU | Consultant uploaded | Consultant comment | Item No | Compliance Task | UU received | UU review & comments | Asset type list
COMPL 1 - On maintenance |  |  |  | 1 | As-Constructed Package Certification form (FOR1101) |  |  | Sewer Pump Sation
|  |  |  | 2A | Land transfer Form 1 |  |  | Water Booster Pump Station
|  |  |  | 2B | Land transfer Form 24 |  |  | PRV
|  |  |  | 2C | Title Search
|  |  |  | 2D | Survey Plan |  |  | Checklist Completed by
|  |  |  | 2E | Mortgage release/ Land tax clearance |  |  | Brett Carruthers
|  |  |  | 2G | Due diligence and valuation report |  |  | Darryl Searle
|  |  |  | 3A | Inspection test reports |  |  | Devendra Yadav
|  |  |  | 3B | Defects list |  |  | George Gadja
|  |  |  | 3C | Construction reports |  |  | John Clayton
|  |  |  | 4A | As constructed - ADAC file |  |  | Michael McCann
|  |  |  | 4B | Statutory declarations |  |  | Sheikh Uddin
|  |  |  | 4C | Form 16 |  |  | Snezana Ilic
|  |  |  | 4D | RPEQ Certificed As constructed Civil drawings
|  |  |  | 4E | Certificed As constructed Mechanical drawings
|  |  |  | 4F | Certified Electrical drawings
|  |  |  | 5 | Maintenance bond
|  |  |  | 6 | Easement forms
|  |  |  | 7 | Payment of outstand fees and charges including infrastructure charges (ICN)
|  |  |  | 8 | Transfer of Energex connection and eletricity bill
|  |  |  | 9 | Signage and locks
Stage | Date Consultant sent to UU | Consultant uploaded | Consultant comment | Item No | Compliance Task | UU received | UU review & comments | Asset type list
COMPL 2 - Off Maintenance |  |  |  | 10 | Off- maintenance inspection and report

## Version Ctrl
Version control/updates
V1.0 | Creation of document | S Syed | 2022-01-01
V1.1 | Administrative changes | S Syed | 2022-01-01
· Using this guideline, page 2
· Milestone 3, Preliminary Design Report acceptance, page 6
V1.2 | Administrative changes | B Brentzell | 2022-03-01
| Updated email address DevelopmentComplexAsset@urbanutilities.com.au | S Syed
· Milestone 3, Design Report acceptance, page 6
V1.3 | Administrative change | A Doyle | 2023-08-01
Updated email address from Changed DCMTEnquiries@urbanutilities.com.au to developmentenquiries@urbanutilities.com.au
V1.4 | Administrative change: | S Uddin | 2024-04-01
Conversion of Word document to Excel
Milestone change:
Compression and reduction of Design milestones
V1.5 | Administrative change:
| updated column formats and security | A Doyle | 2024-08-01

## working sheet
Type of Asset | Reason | Who | Options
| IR | Consultant | N/A | Submitted
Sewer Pump Station | Lodgement of milestone | UU | Yes | Not yet received
Water Booster Pump Station | Milestone approved with conditions
PRV | Response to IR
uploaded and reviewed?
DO NOT TOUCH
Yes
No